## 2023 READ ME
Storm Overflows |  | Version | Date | Update Description
Introduction |  | V1 | 2024-03-31 | Version 1 original document
We are now able to report on Event Duration Monitoring (EDM) installed at all 1,295 of our storm overflows.
What are Storm Overflows, what impact do they have and why do we have them?
Storm Overflows (SOs) exist because most properties were built at a time when drains serving a new property carried both rainwater and sewage (a.k.a. combined sewers). Heavy or prolonged rainfall or high groundwater levels can rapidly increase the flow in a combined sewer until the amount of water exceeds sewer capacity. Storm overflows act as relief valves, allowing excess stormwater to be released to rivers or the sea. This protects properties from flooding and prevents sewage backing up into streets and homes during heavy storm events. As storm overflows should only discharge liquid dominated by rainwater, any foul water released from them will be very dilute because of the large volumes of rainwater within the system. Flows are further diluted by the receiving watercourses that will also be swollen by the same heavy rain. Many storm overflows are fitted with screens or scumboards that prevent debris entering the watercourse or have attenuation tanks which also protect water quality. Pollution incidents are very rarely caused by a storm overflow which has operated correctly, as there is no significant environmental impact in terms of ammonia, suspended solids and biochemical oxygen demand. | Find out more about our Storm Overflows
How groundwater affects Storm Overflow performance
During prolonged wet periods groundwater levels can rise above sewers and drains. This is especially true of chalk strata which is prevalent in the area served by Wessex Water. Any cracks or holes in private drains or our sewers or manhole chambers can allow the groundwater to infiltrate and can inundate the system. This can cause prolonged surcharging of the sewers until the groundwater level recedes. The discharges are very dilute and sampling shows that there is minimal impact on the environment. Without the overflows, this would lead to restricted toilet use for customers as well as property flooding. Our Drainage and Wastewater Management Plan (DWMP) webpages shows areas vulnerable to groundwater inundation and also includes reports and videos related to infiltration reduction plans. These show our ongoing programmes of inspection and making sewers watertight. However about two thirds of the underground pipe network is owned by private individuals. Our storm overflow at Shrewton water recycling centre discharged for more hours than any other overflow in the Wessex Water region. The videos linked to the right show what that discharge looks like. Tests show it is cleaner than standards set for treated sewage discharges. | Infiltration reduction plans and the challenges of groundwater management
https://www.youtube.com/watch?v=iB0eGbgQPXo
https://www.youtube.com/watch?v=eipbAXBpnis
How can I find out more information about when Storm Overflows operate?
Our Coastwatch overflow notification system provides near real-time information of when storm overflows have operated at designated coastal bathing waters and at amenity waters used regularly for recreation where we know there might be a deterioration in water quality as a result of discharges. This notification system operates all-year round. | Link to Coastwatch
This data is also supplied to the Surfers Against Sewage which they use in their SaferSeasApp. | Safer Seas Service • Surfers Against Sewage (sas.org.uk)
Information on the location and historical frequency of operation of Storm Overflows, and dates for installing monitors where none currently exist, can also be found on our interactive Drainage and Wastewater Management Plan Mapping Portal. | Link to Drainage and Wastewater Management Plan Mapping Portal
In 2024, we will be publishing live storm overflow operating data for all storm overflows
Environmental Impact from Storm Overflows
The main worksheet contains information about the impact of storm overflows on the environment.
There is currently not a significant amount of data that associates poor water quality classification with the impact of storm overflows. 7 separate waterbodies in the Wessex Water region have 'confirmed', 'probable' or 'suspected' reasons for waterbodies failing good ecological status is due to storm overflows. | EA river water quality information
Water quality impact data is a key factor for future investment in storm overflow improvements.
How are Wessex Water reducing the numbers and impact of Storm Overflow discharges (and SODRP)
We have a planned investment programme between now and 2050 to address storm overflows. The plans for each overflow are presented in the 'Overflows summary' worksheet
Since 2000, we have invested £181 million to upgrade more than 582 storm overflows and are spending £150m between 2020-2025 on further improvements. We have also worked with farmers on catchment management to help reduce run-off, which is a major factor in river/sea water quality, as well as tackling misconnections and educating our customers on how to avoid sewer blockages that cause pollutions. | Find out more about misconnections
Our short term plan (called Storm Overflows Improvement Plan 2022-2025) is available as a pdf to download from our website. | Storm overflows (wessexwater.co.uk)
Our longer term plan is to meet and then beat the targets set down in the Environment Act 2021. This sets different standards for different overflows according to their likely impact on the environment and whether they are near bathing waters. We have prioritised our long term investment plan based on the direction given in the Storm Overflow Discharge Reduction Plan (SODRP). | Storm_Overflows_Discharge_Reduction_Plan.pdf (publishing.service.gov.uk)
We support the ambition to reduce impacts from storm overflows and in an ideal world, we would not have combined sewerage systems at all. However, this is a complex problem that took centuries to create and which will take many years to address. We have prepared a document called Overview of Sewer System and Storm Overflows to explain the issues and our thoughts on how to address them. This is available to download from our Storm Overflows webpage | Storm overflows (wessexwater.co.uk)
How we will update this data
Data from our Event Duration Monitoring is collated for an annual return to the Environment Agency in January/February each year, covering the previous calendar year. Data will be updated to this spreadsheet in the following Spring and published on our Drainage and Wastewater Management Plan (DWMP) website. If we find previously reported data is incorrect, we update it in this file. Hence, it is possible for a small number of spill counts in a particular year to vary from what was submitted to EA originally in the annual report. | Link to our Drainage and Wastewater Management Plan
Further Questions or Queries?
If you have any additional questions about Storm Overflows, there is a FAQ section on our storm overflows webpage. | Storm overflows (wessexwater.co.uk)
Glossary
SO: Storm Overflow - Storm Overflows can be on Combined Sewers (Combined Sewer Overflows or CSOs) or at pumping stations or at water recycling centres
EDM: Event Duration Monitoring (the term used to describe the monitors that are being installed at each SO)
SOAF: Storm Overflow Assessment Framework (process for assessing options, costs and benefits and delivering improvements for Storm Overflows that discharge frequently)
WRC: Water Recycling Centre (also known as a Sewage Treatment Works. Most of what arrives at a WRC is water and is processed to return it to the environment)
WINEP: Water Industry National Environment Programme (a set of outputs set each five years that the water company delivers to achieve environmental outcomes)
DWMP: Drainage and Wastewater Management Plans (a new obligation on companies to demonstrate the need for future investment to meet maintenance needs and enhancements to current sewerage assets to protect and improve the environment)
12/24 Counted Discharges - this refers to the standard 12-24hr counting method. This basically equates to 'number of 24 hr periods that saw some discharge activity from an individual overflow'.

## Trends
Year | Nr. Monitored Overflows | Av. Discharge Count | Sum Discharge Count | Av. Discharge Hrs | Sum Discharge Hrs | % reduction from 2020 | Av. % Operational
2020 | 971 | 30 | 29014 | 244 | 236909 | - | 97%
2021 | 1049 | 23 | 23635 | 144 | 150978 | 37% | 97.8%
2022 | 1182 | 19 | 21878 | 110 | 129957 | 45% | 98%
2023 | 1295 | 32 | 41455 | 288 | 372341 | -57.17% | 98.4%

## Overflows Summary
Overflow ID | Site Name | EA Permit Reference | Storm Discharge Asset Type | Treatment Method (over & above storm tank settlement / screening) | Overall Level of Treatment | What's getting in the sewer causing it to discharge? | District Council | Westminster Constituency | Outlet Discharge NGR | WFD Waterbody ID (Cycle 2) | WFD Waterbody Catchment Name (Cycle 2) | Receiving Water / Environment | Shellfish Water | Bathing Water | Bathing Water profile 1 (web link) | Bathing Water profile 2 (web link) | Initial EDM Commission Date | 2020 spill count | 2021 spill count | 2022 spill count | 2023 spill count | 2023 Total Duration (hrs) all spills prior to processing through 12-24h count method | 2023 EDM Operation - % of reporting period EDM operational | Long-term average spill count | No. full years EDM data (years) | EDM Operation - Reporting % - Primary Reason <90% | EDM Operation - Action taken / planned - Status & timeframe | High Spill Frequency - Operational Review - Primary Reason | High Spill Frequency - Action taken / planned - Status & timeframe | High Spill Frequency - Environmental Enhancement - Planning Position (Hydraulic capacity) | Latest Aesthetic impact survey date | Aesthetic impact assessment | Latest Invertebrate impact survey date | Invertebrate impact assessment | Latest WQ impact survey date | WQ impact assessment | Other impact data collected | Comments | Ecological status of waterbody (web link) | Is the storm overflow located in a waterbody where the Reason for Not Achieving Good (RNAG) Ecological Status has been linked to Storm Overflows? Yes/No | Improvement date planned to 2025 | Improvement detail planned to 2025 | Long-term improvement date planned | Long-term improvement plan | Long-term improvement plan detail
13022S | BISHOPS LYDEARD STORM TANK | 102049 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST1826028760 | GB108052021390 | Back Stream | BACK STREAM |  |  |  |  | Commissioned in 2018 - full year data expected | 26 | 19 | 8 | 23 | 278 | 99.9254 | 23 | 5 (installed 2018) | [7 empty] | 2020-03-06 | Field based assessment - No impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021390 | No | 2025-02-01 | Additional 28m3 storm storage installed. | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Additional 28m3 storm storage installed. Planned improvement completion date 2045 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16762C | SALTFORD SALTFORD HILL | 102125 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6900366654 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 94 | 51 | 42 | 65 | 70.7667 | 99.9228 | 56.125 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2020-05-13 | No sewage litter or sewage fungus | 2020-05-13 | N/A - WQM required | 2022-03-01 | Water Quality Modelling shows that the WFD Status Class at the 99%ile level for BOD and Ammonia is High ‘with’ or ‘without’ all Bath FSOs |  | Multiple overflows so unsuitable for invertebrate assessment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No | 2025-03-25 | Construct an additional 50m3 storm storage tank. | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Construct an additional 50m3 storm storage tank. Planned improvement completion date 2035 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16759C | BATHFORD OSTLING LANE | 100504/CS/01 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST7857066960 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 78 | 63 | 44 | 62 | 106.0333 | 99.7728 | 61.6667 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2020-11-30 | No sewage litter or sewage fungus |  | N/A | 2022-03-01 | Water Quality Modelling shows that the WFD Status Class at the 99%ile level for BOD and Ammonia is High ‘with’ or ‘without’ all Bath FSOs |  | Unable to locate outfall, investigation ongoing | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No | 2024-06-12 | Construct an additional c100m3 of storage in Bathford to reduce discharges to the river Avon from 66/year to c9/year. | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Construct an additional c100m3 of storage in Bathford to reduce discharges to the river Avon from 66/year to c9/year. Planned improvement completion date 2035 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13027S | BOURTON SILTON STORM TANK | 040010 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | NORTH DORSET | North Dorset Co Const | ST7863929787 | GB108043022490 | Stour (Headwaters) | RIVER STOUR |  |  |  |  | Commissioned in 2020 - full year data expected |  | 122 | 104 | 159 | 2463.4464 | 99.9999 | 128.3333 | 3 (installed 2020) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [5 empty] | 2022-06-22 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022490 | No | 2025-03-31 | Increase the biological treatment capacity from 6.8l/s to 13l/s. | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Increase the biological treatment capacity from 6.8l/s to 13l/s. Planned improvement completion date 2040 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13142B | HARDINGTON MANDEVILLE WIMBOROUGH LANE INLET | 070154 | Inlet SO at WwTW |  | Diluted | Groundwater | SOUTH SOMERSET | Yeovil Co Const | ST5049712163 | GB108052015310 | Chinnock BK | CHINNOCK BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 60 | 47 | 45 | 78 | 1225.5 | 99.9971 | 57.5 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2022-09-27 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015310 | No | 2024-07-31 | Increase the storm storage volume by 27m3. | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Increase the storm storage volume by 27m3. Planned improvement completion date 2040 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13271S | SHILLINGSTONE STORM TANK | 401340 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | NORTH DORSET | North Dorset Co Const | ST8383010560 | GB108043016051 | Stour (Middle u/s Pimperne Brook) | STOUR(S) |  |  |  |  | Commissioned in 2020 - full year data expected |  | 67 | 51 | 131 | 1822.2833 | 99.7306 | 83 | 3 (installed 2020) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016051 | No | 2025-01-27 | Increase the treatment capacity of Shillingstone WRC by about 40% from 19.5l/s to 27.5l/s. | 2025 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Increase the treatment capacity of Shillingstone WRC by about 40% from 19.5l/s to 27.5l/s. Planned improvement completion date 2025 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13214S | MILVERTON STORM TANK | 070076 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | TAUNTON DEANE | Taunton Deane Co Const | ST1337025890 | GB108052015510 | Hillfarrance Bk | HILLFARRANCE BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 64 | 72 | 58 | 109 | 1351 | 100 | 62 | 6 (installed 2017) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2021-03-23 | No sewage litter or sewage fungus | 2023-10-16 | Lab assessment - No impact |  |  |  | Too turbid for aesthetic impact assessment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015510 | No | 2024-10-17 | Increase total storm storage to 168m3 by converting a redundant settlement tank into a stormwater storage tank. | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Increase total storm storage to 168m3 by converting a redundant settlement tank into a stormwater storage tank. Planned improvement completion date 2040 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13349S | WIMBORNE BROOK ROAD STORM TANK | 400972 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | EAST DORSET | Mid Dorset and North Poole Co Const | SZ0241099110 | GB108043011040 | Stour (Lower) | RIVER STOUR(S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 33 | 75 | 1196.1333 | 100 | 54 | 1 (installed 2022) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011040 | No | 2024-06-28 | Increase total storm storage to 2,213m3 by constructing a new stormwater storage tank. | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Increase total storm storage to 2,213m3 by constructing a new stormwater storage tank. Planned improvement completion date 2045 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13366S | YEOVIL SHERBORNE ROAD (PEN MILL) STORM TANK | 101331 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5736616247 | GB108052015681 | Yeo Us Over Compton | RIVER YEO |  |  |  |  | Commissioned in 2019 - full year data expected | 32 | 23 | 29 | 38 | 307.8758 | 100 | 25.7143 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015681 | No | 2024-09-06 | Increase total storm storage to 5,503 m3 by constructing new primary settlement tanks to improve treatment resilience then converting existing primary tanks into stormwater storage tanks. | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Increase total storm storage to 5,503 m3 by constructing new primary settlement tanks to improve treatment resilience then converting existing primary tanks into stormwater storage tanks. Planned improvement completion date 2035 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13158S | HURDCOTT STORM TANK | 040044 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | SALISBURY | Salisbury Co Const | SU1684033590 | GB108043022390 | Bourne (Hampshire Avon) | RIVER BOURNE |  |  |  |  | Commissioned in 2017 - full year data expected | 190 | 163 | 149 | 253 | 3980.25 | 100 | 182.5 | 6 (installed 2017) |  |  | Performance - GW inundation | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2023-09-05 | No sewage litter or sewage fungus | 2023-09-05 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022390 | No | 2024-07-31 | New bio-swale constructed to provide improvement to storm overflows from site. | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: New bio-swale constructed to provide improvement to storm overflows from site. Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13192S | MAIDEN NEWTON DORCHESTER ROAD STORM TANK | 041353 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | WEST DORSET | West Dorset Co Const | SY6025397176 | GB108044009691 | Frome Dorset (Lower) u/s Louds Mill Dorchester | RIVER FROME |  |  |  |  | Commissioned in 2019 - full year data expected | 108 | 64 | 27 | 112 | 2106.75 | 99.6553 | 68.6 | 4 (installed 2019) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009691 | No | 2025-03-31 | New nature based solution for delivery by 2030. | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: New nature based solution for delivery by 2030. Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13817C | CHIPPENHAM 22 LONG CLOSE | Unpermitted | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | Chippenham Co Const | ST9278802830 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | Avon (Brist) conf R Marden to conf Semington Bk |  |  |  |  | Dec 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No | 2024-10-09 | Provide storage tank and close one of two overflows | 2025 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Provide storage tank and close one of two overflows.
16582C | CHIPPENHAM 16 LONG CLOSE | 100081 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | Chippenham Co Const | ST9277872873 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2021 - full year data expected |  | 27 | 26 | 42 | 77.1 | 99.9745 | 31.6667 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No | 2024-10-09 | Provide storage tank and close one of two overflows | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Provide storage tank and close one of two overflows.
14219B | UPTON SANDY LANE | 402036 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | Mid Dorset and North Poole Co Const | SY9836092200 | 68 | Not part of a river WB catchment | LYTCHETT BAY(E) |  |  |  |  | Commissioned in 2017 - full year data expected | 36 | 23 | 28 | 39 | 126.9167 | 99.9896 | 29.8571 | 6 (installed 2017) | [13 empty] | Not part of a river WB catchment | No | 2024-05-17 | Provision of 150m3 storm storage & increase FPF from 5l/s to 9l/s to reduce storm overflows to the environment. | 2024 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Provision of 150m3 storm storage & increase FPF from 5l/s to 9l/s to reduce storm overflows to the environment. Planned improvement completion date 2024 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16562C | FRAMPTON COTTERELL WEST END NIGHTINGALES BRIDGE | 101031 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6626081350 | GB109053027820 | Frome (Brist) - conf Laddon Bk to conf Folly Bk | RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 75 | 48 | 40 | 92 | 922.6333 | 94.3371 | 62.3333 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP or Green Recovery | 2021-04-13 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027820 | No | 2024-08-06 | Provision of 180m3 storage to be provided reducing spills to approximately 10.5 / year. | 2024 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Provision of 180m3 storage to be provided reducing spills to approximately 10.5 / year. Planned improvement completion date 2024 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16605C | BOX VALENS TERRACE | 101695 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST8232768729 | GB109053027380 | By Bk - conf Doncombe Bk to conf R Avon (Brist) | BY BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 76 | 46 | 38 | 54 | 222.4667 | 99.6922 | 50 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2021-03-29 | No sewage litter or sewage fungus |  | N/A | 2022-08-01 | UPM - RAT Level 1 WQ gives no impact |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027380 | No | 2026-03-10 | Provision of 2360m3 of storm storage to reduce spills to the environment to below 10 / year. | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Provision of 2360m3 of storm storage to reduce spills to the environment to below 10 / year. Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14431B | BISHOP SUTTON | EPRZP3821GK | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST5814260252 | GB109053021852 | Chew - Chew Valley Lake to conf Winford Brook | A TRIBUTARY OF THE RIVER CHEW |  |  |  |  | Commissioned in 2016 - full year data expected | 97 | 70 | 60 | 76 | 161.4533 | 100 | 70.5 | 7 (installed 2016) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP or Green Recovery | 2019-09-07 | No sewage litter or sewage fungus | 2018-03-16 | Lab assessment - Impact | 2021-12-09 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021852 | No | 2024-08-14 | Provision of 250m3 storm storage to reduce spills to approximately 4/year. | 2024 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Provision of 250m3 storm storage to reduce spills to approximately 4/year. Planned improvement completion date 2024 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16914C | WARMINSTER WEYMOUTH STREET R/O 23 IN PLEASURE GARDENS NEAR SWIMMING POOL | 401092 | SO on sewer network |  | Diluted | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8734844869 | GB108043022540 | Wylye Trib (The Were or Swan) | RIVER WYLE VIA THE WERE (SWS) |  |  |  |  | Commissioned in 2019 - full year data expected | 122 | 54 | 56 | 75 | 100.8167 | 99.9848 | 65.2857 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP or Green Recovery | 2020-03-26 | Sewage litter present, no sewage fungus | 2020-03-26 | Lab assessment - No impact | 2022-08-01 | UPM - RAT Level 1 WQ gives no impact |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022540 | No | 2024-09-18 | Provision of 300m3 storage to be provided to reduce spills to below 10 / year. | 2024 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Provision of 300m3 storage to be provided to reduce spills to below 10 / year. Planned improvement completion date 2024 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13223S | NORTH PETHERTON STORM TANK | 101640 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3005932637 | GB108052021360 | Petherton Stream | PETHERTON STREAM |  |  |  |  | Commissioned in 2017 - full year data expected | 56 | 47 | 38 | 80 | 602.5667 | 99.9056 | 55.1667 | 6 (installed 2017) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP or Green Recovery | 2018-05-04 | No sewage litter or sewage fungus | 2018-05-04 | Lab assessment - No impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021360 | No | 2024-10-24 | Provision of 400m3 storage by constructing a new stormwater tank. | 2024 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Provision of 400m3 storage by constructing a new stormwater tank. Planned improvement completion date 2024 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16561C | WINTERBOURNE WATLEYS END IN FIELD OFF FACTORY ROAD | 103072 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6604981072 | GB109053027820 | Frome (Brist) - conf Laddon Bk to conf Folly Bk | RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 110 | 79 | 60 | 124 | 1155.8 | 98.882 | 79.7143 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP or Green Recovery | 2018-04-13 | No sewage litter or sewage fungus | 2017-11-16 | WQM required |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027820 | No | 2025-02-12 | Provision of 480m3 storage to be provided reducing spills to approximately 18 / year. | 2025 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Provision of 480m3 storage to be provided reducing spills to approximately 18 / year. Planned improvement completion date 2025 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16092C | BATH FOX HILL O/S WOODLANDS COTTAGE | 010936 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7538464296 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 51 | 41 | 33 | 50 | 25.5 | 100 | 44.5 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP or Green Recovery | 2020-11-30 | No sewage litter or sewage fungus |  | N/A | 2022-03-01 | Water Quality Modelling shows that the WFD Status Class at the 99%ile level for BOD and Ammonia is High ‘with’ or ‘without’ all Bath FSOs |  | Multiple overflows so unsuitable for invertebrate assessment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No | 2024-08-09 | Provision of 99m3 storage to be provided to reduce spills to below 10 / year. | 2024 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Provision of 99m3 storage to be provided to reduce spills to below 10 / year. Planned improvement completion date 2024 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14047B | COATE SPANIELS BRIDGE | NPSWQD008925 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | KENNET | Devizes Co Const | SU0420162218 | GB108043022430 | Etchilhampton Water | TRIBUTARY OF RIVER AVON |  |  |  |  | Commissioned in 2017 - full year data expected | 142 | 78 | 96 | 193 | 4210.9833 | 99.9049 | 102.8333 | 6 (installed 2017) |  |  | Performance - GW inundation | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2020-11-25 | Sewage litter present, no sewage fungus | 2020-11-25 | Lab assessment - No impact | 2021-11-16 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022430 | No | 2024-07-31 | Provision of a new reedbed and re-routing of the existing watercourse to improve biodiversity. | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Provision of a new reedbed and re-routing of the existing watercourse to improve biodiversity. Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16866C | PORTLAND HIGH STREET | 041274 | SO on sewer network |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6838473264 | GB620806560000 | Lyme Bay East | WEST BAY (COASTAL) |  |  |  |  | Commissioned in 2017 - full year data expected | 17 | 17 | 16 | 31 | 4.3667 | 99.8747 | 18.4286 | 6 (installed 2017) | [5 empty] | 2023-10-04 | Sea outfall - N/A |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620806560000 | No | 2025-12-31 | Provision of additional storm capacity to existing combined network. Separation of surface water connections within catchment. Diversion of overflow into new capacity created within the sewer. | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Provision of additional storm capacity to existing combined network. Separation of surface water connections within catchment. Diversion of overflow into new capacity created within the sewer. Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13316C | TOLLER PORCORUM TOLLER LANE INLET | 400607 | Inlet SO at WwTW |  | Diluted | A combination of rainwater and groundwater | WEST DORSET | West Dorset Co Const | SY5669897970 | GB108044009800 | Hooke | RIVER HOOKE |  |  |  |  | Commissioned in 2019 - full year data expected | 39 | 47 | 43 | 76 | 691.75 | 99.8345 | 46.8 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009800 | No | 2024-12-31 | Provision of an additional 27m3 stormwater storage tank. | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Provision of an additional 27m3 stormwater storage tank. Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13152S | HOLDENHURST RIVERSIDE AVENUE STORM TANK | 401065 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | CHRISTCHURCH | Christchurch Co Const | SZ1360095050 | GB108043011040 | Stour (Lower) | RIVER STOUR (S) |  | CHRISTCHURCH AVON BEACH/CHRISTCHURCH FRIAR'S CLIFF | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=avon%20b&site=ukk2201-18800 | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=friar&site=ukk2201-18750 | Commissioned in 2016 - full year data expected | 24 | 14 | 16 | 32 | 124.3116 | 100 | 19.125 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011040 | No | 2024-09-17 | Provision of an additional 9,000m3 of storm storage (total volume of 29,800m3) to reduce discharges to 2 per Bathing Season (summer). | 2024 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Provision of an additional 9,000m3 of storm storage (total volume of 29,800m3) to reduce discharges to 2 per Bathing Season (summer). Planned improvement completion date 2024 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16556C | FRAMPTON COTTERELL ST PETERS CHURCH (NW) CHURCH ROAD | 103070 | SO on sewer network |  | Diluted | A combination of rainwater and groundwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6676181904 | GB109053027820 | Frome (Brist) - conf Laddon Bk to conf Folly Bk | RIVER FROME |  |  |  |  | Commissioned in 2019 - full year data expected | 68 | 73 | 56 | 104 | 1137.0833 | 99.9782 | 71.1429 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP or Green Recovery | 2021-04-13 | Sewage litter present, no sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027820 | No | 2024-06-06 | Provision of an additional c225m3 of new storage to reduce discharges from 70/year to c13/year. | 2024 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Provision of an additional c225m3 of new storage to reduce discharges from 70/year to c13/year. Planned improvement completion date 2024 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13331C | WELLOW INLET | 010092 | Inlet SO at WwTW |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST7442858143 | GB109053022271 | Wellow Bk - Snails Bk to Bristol Avon | WELLOW BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 29 | 19 | 28 | 45 | 244.3667 | 100 | 34.1667 | 6 (installed 2017) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other improvements - non-WINEP/Green Recovery | 2021-11-11 | No sewage litter or sewage fungus | 2021-11-11 | Lab assessment - No impact | 2022-12-01 | UPM - RAT Level 1 WQ gives No Impact |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022271 | No | 2025-03-31 | Provision of150m3 storm storage to be provided to reduce the operation of the overflow. | 2025 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Provision of150m3 storm storage to be provided to reduce the operation of the overflow. Planned improvement completion date 2025 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13307S | TETBURY STORM TANK | 102818 | Storm tank at WwTW - with treatment |  | Diluted and partially treated | A combination of rainwater and groundwater | COTSWOLD | The Cotswolds Co Const | ST8955292456 | GB109053027800 | Tetbury Avon - source to conf unnamed trib | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 73 | 58 | 41 | 138 | 2598 | 99.9092 | 79.8333 | 5 (installed 2018) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2023-10-24 | Sewage fungus and sewage litter present | 2020-03-27 | Lab assessment - No impact |  |  |  | RICT unsuitable | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027800 | No | 2024-07-01 | Refurbishing the reedbeds to enable allow settled stormwater receive biological treatment. | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Refurbishing the reedbeds to enable allow settled stormwater receive biological treatment. Planned improvement completion date 2040 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15334B | CHARLTON ADAM | 101604 | Storm discharge at pumping station |  | Diluted | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST5419728840 | GB108052015140 | Cary - source to conf with KSD | TRIB OF THE RIVER CARY |  |  |  |  | Commissioned in 2020 - full year data expected |  | 0 | 1 | 1 | 0.11666 | 99.8992 | 0.66667 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015140 | No | 2024-05-31 | Seal sewer pipes in Charlton Adam and Keinton Mandeville to prevent groundwater entering the system. | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Seal sewer pipes in Charlton Adam and Keinton Mandeville to prevent groundwater entering the system. Planned improvement completion date 2023 or before - Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14585B | EDINGTON BROADMEAD LANE (SOM) | NPSWQD006726 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3860740138 | GB108052021181 | South Drain | TRIB OF NIDON RHYNE |  |  |  |  | Commissioned in 2018 - full year data expected | 97 | 62 | 36 | 89 | 1901 | 99.8116 | 50.875 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue |  |  | 2020-11-17 | Lab assessment - No impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021181 | No | 2025-03-31 | Seal sewer pipes in Edington to prevent groundwater entering the system. | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Seal sewer pipes in Edington to prevent groundwater entering the system. Planned improvement completion date 2040 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15497C | MARTINSTOWN B3159 | 401520 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | WEST DORSET | West Dorset Co Const | SY6536088740 | GB108044010060 | South Winterbourne | THE SOUTH WINTERBOURNE(S) |  |  |  |  | Commissioned in 2020 - full year data expected | 145 | 104 | 49 | 171 | 1869.5036 | 100 | 117.25 | 3 (installed 2020) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2020-11-24 | No sewage litter or sewage fungus | 2020-11-24 | Lab assessment - No impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010060 | No | 2024-05-31 | Seal sewer pipes in Martinstown to prevent groundwater entering the system. | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Seal sewer pipes in Martinstown to prevent groundwater entering the system. Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17002C | OLD CLEEVE BYE FARM NEW SO | 102030 | SO on sewer network |  | Diluted | Groundwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | ST0512041660 | GB108051020560 | Washford - Lower | WASHFORD RIVER (S) |  | BLUE ANCHOR WEST | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=blue%20a&site=ukk2305-35200 |  | Commissioned in 2016 - full year data expected | 78 | 83 | 65 | 94 | 767.3744 | 99.1185 | 69.375 | 7 (installed 2016) |  |  | Performance - GW inundation | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2020-04-20 | No sewage litter or sewage fungus | 2020-04-20 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108051020560 | No | 2025-03-31 | Seal sewer pipes in Roadwater to prevent groundwater entering the system. | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Seal sewer pipes in Roadwater to prevent groundwater entering the system. Planned improvement completion date 2035 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13265B | SHAPWICK SOMERSET | 072077 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST4175038740 | GB108052021181 | South Drain | STH DRAIN-TRIB OF LWR BRUE (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 40 | 30 | 34 | 66 | 1171.1278 | 99.4389 | 42.5 | 5 (installed 2018) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021181 | No | 2025-03-31 | Seal sewer pipes in Shapwick to prevent groundwater entering the system. | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Seal sewer pipes in Shapwick to prevent groundwater entering the system. Planned improvement completion date 2050 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13066S | CHRISTCHURCH STONEY LANE STORM TANK | 401355 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | CHRISTCHURCH | Christchurch Co Const | SZ1620093040 | GB520804315900 | CHRISTCHURCH HARBOUR | RIVER AVON(E) |  | CHRISTCHURCH AVON BEACH/CHRISTCHURCH FRIAR'S CLIFF | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=avon%20b&site=ukk2201-18800 | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=friar&site=ukk2201-18750 | Commissioned in 2016 - full year data expected | 43 | 26 | 10 | 56 | 922.3293 | 99.9958 | 23.25 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB520804315900 | No | 2025-03-31 | Seal sewer pipes in Sopley to prevent groundwater entering the system. | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Seal sewer pipes in Sopley to prevent groundwater entering the system. Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13319S | UBLEY FROG LANE STORM TANK | 101480 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST5241158514 | GB109052021640 | Yeo - source to conf Congresbury Yeo | CONGRESBURY YEO, TRIB OF LAKE |  |  |  |  | Commissioned in 2019 - full year data expected | 120 | 61 | 69 | 113 | 2233.2667 | 99.153 | 91.6667 | 4 (installed 2019) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2021-03-11 | Sewage fungus present no sewage litter | 2021-03-11 | Incomplete |  |  |  | No upstream inverts samples | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021640 | Yes | 2024-09-12 | Seal sewer pipes in Sopley to prevent groundwater entering the system. | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Seal sewer pipes in Sopley to prevent groundwater entering the system. Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15084B | VERWOOD POTTERNE WAY | 401155 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | EAST DORSET | North Dorset Co Const | SU0985007550 | GB108043016090 | Crane (Dorset) | RIVER CRANE (S) |  |  |  |  | Commissioned in 2017 - full year data expected | 86 | 32 | 24 | 56 | 299.8333 | 99.9994 | 49.5 | 6 (installed 2017) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2018-03-20 | No sewage litter or sewage fungus | 2018-03-20 | Lab assessment - No impact |  |  |  | RICT analysis complete (Moderate) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016090 | No | 2025-03-31 | Seal sewer pipes in Verwood to prevent groundwater entering the system. | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: Seal sewer pipes in Verwood to prevent groundwater entering the system. Planned improvement completion date 2035 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13048S | CASTLE CARY NEAR DIMMER STORM TANK | 071220 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST6269231831 | GB108052015140 | Cary - source to conf with KSD | RIVER CARY |  |  |  |  | Commissioned in 2019 - full year data expected | 22 | 24 | 25 | 60 | 594.5 | 99.9436 | 32.75 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015140 | No | 2025-03-31 | The treatment capacity will be increased by a third from 25.5l/s to 34l/s by adding primary, biological, and final settlement tanks to accommodate additional flows. | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: The treatment capacity will be increased by a third from 25.5l/s to 34l/s by adding primary, biological, and final settlement tanks to accommodate additional flows. Planned improvement completion date 2045 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13140S | HALSTOCK WATERY LANE STORM TANK | 071221 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | WEST DORSET | West Dorset Co Const | ST5429408165 | GB108052015520 | Sutton Bingham Stream - East Arm | TRIBUTARY OF THE RIVER YEO |  |  |  |  | Commissioned in 2019 - full year data expected | 157 | 103 | 87 | 148 | 2585.25 | 99.7317 | 127 | 4 (installed 2019) |  |  | Performance - GW inundation | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2020-10-09 | No sewage litter or sewage fungus | [6 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015520 | No | 2024-11-25 | The treatment capacity will be more than doubled from 2.3l/s to 4.8/s. This will require a new inlet pumping station and new primary and humus settlement tanks. | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2025: The treatment capacity will be more than doubled from 2.3l/s to 4.8/s. This will require a new inlet pumping station and new primary and humus settlement tanks. Planned improvement completion date 2035 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13016S | SALTFORD MEAD LANE STORM TANK | 102272 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6950068550 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2016 - full year data expected | 92 | 49 | 44 | 86 | 909.4333 | 99.8805 | 59.125 | 7 (installed 2016) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2020-05-13 | No sewage litter or sewage fungus | 2020-05-13 | Lab assessment - No impact | 2022-03-01 | Water Quality Modelling shows that the WFD Status Class at the 99%ile level for BOD and Ammonia is High ‘with’ or ‘without’ all Bath FSOs |  | RICT analysis also complete (Impact high) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No | 2026-12-31 | The treatment capacity of the WRC at Saltford (which serves the city of Bath) will be increased from 580l/s to 802l/s by constructing two new primary settlement tanks, a new activated sludge plant to provide biological treatment capacity and two new final settlement tanks. Construction underway. | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2026: The treatment capacity of the WRC at Saltford (which serves the city of Bath) will be increased from 580l/s to 802l/s by constructing two new primary settlement tanks, a new activated sludge plant to provide biological treatment capacity and two new final settlement tanks. Planned improvement completion date 2035 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13274S | SHOSCOMBE STORM TANK | 010080 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST7168755846 | GB109053022271 | Wellow Bk - Snails Bk to Bristol Avon | WELLOW BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 11 | 7 | 4 | 69 | 619.85 | 91.3882 | 16.8333 | 6 (installed 2017) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2023-09-28 | No sewage litter or sewage fungus | 2023-09-28 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022271 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2026: The treatment capacity will be increased by 60% from 10l/s to 16l/s, and total storm storage will be increased to 165m3 (existing is 48m3) by converting a redundant settlement tank into a stormwater storage tank. Planned improvement completion date 2035 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13013S | AVONMOUTH KINGSWESTON LANE STORM TANK | 102107 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | BRISTOL | Bristol North West Boro Const | ST5191080700 | GB530905415405 | BRISTOL AVON | SEVERN ESTUARY(E) |  | CLEVEDON BEACH | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=cleved&site=ukk1202-36000 |  | Commissioned pre-2016 - full year data expected | 131 | 93 | 86 | 148 | 2336.4833 | 99.9909 | 100.4286 | 10+ (installed pre-2013) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2022-03-14 | No sewage litter or sewage fungus |  | TRAC site - N/A |  |  |  | No sewage fungus assessment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No | 2028-03-31 | The treatment capacity will be increased from 3,472 l/s to 5,700 l/s. Construction will be part completed by 2025 and we expect full commissioning by the end of 2028. | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | By end of 2028: The treatment capacity will be increased from 3,472 l/s to 5,700 l/s. Construction will be part completed by 2025 and we expect full commissioning by the end of 2028. Planned improvement completion date 2035 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13275S | SHREWTON STORM TANK | 040080 | Storm tank at WwTW - with treatment | Reed bed | Fully treated | Groundwater | SALISBURY | Salisbury Co Const | SU0743742649 | GB108043022570 | Till (Hampshire Avon) | RIVER TILL |  |  |  |  | Commissioned in 2019 - full year data expected | 201 | 184 | 136 | 262 | 6183.9167 | 99.7831 | 154.8182 | 4 (installed 2019) |  |  | Performance - GW inundation | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2022-04-08 | No sewage litter or sewage fungus | 2022-04-08 | Lab assessment - No impact |  |  | See case study page | Has wetland treatment. See case study page. Measured 2km downstream at the perennial head Till at Winterbourne Stoke. RICT analysis also complete (LOW). | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022570 | No | 2022-10-31 | Existing reed beds were upgraded for additional treatment of the settled storm overflow. We have also been sealing sewer pipes in Shrewton to prevent groundwater entering the system. | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Existing reed beds were upgraded for additional treatment of the settled storm overflow. We have also been sealing sewer pipes in Shrewton to prevent groundwater entering the system. Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13256S | RODE STORM TANK | 011560 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | MENDIP | Somerton and Frome Co Const | ST8039554549 | GB109053021840 | Somerset Frome conf with Mells to conf B. Avo | SOMERSET FROME(S) |  |  |  |  | Commissioned in 2016 - full year data expected | 49 | 47 | 61 | 102 | 1429.1313 | 99.9533 | 42.5 | 7 (installed 2016) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2018-11-16 | No sewage litter or sewage fungus | 2018-11-16 | Lab assessment - No impact |  |  |  | RICT analysis also complete (Moderate) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021840 | No | 2023-11-07 | Flow to Full treatment capacity was increased from 6.1l/s to 10 l/s. | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Flow to Full treatment capacity was increased from 6.1l/s to 10 l/s. Planned improvement completion date 2040 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13268S | SHERBORNE WEST MILL LANE STORM TANK | 070099 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | ST6301515348 | GB108052015630 | Yeo | RIVER YEO |  |  |  |  | Commissioned in 2018 - full year data expected | 9 | 4 | 13 | 59 | 453.5822 | 99.9092 | 21.8333 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015630 | No | 2022-03-01 | Increase total storm storage to 482m3 by constructing a new 175m3 stormwater tank. | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Increase total storm storage to 482m3 by constructing a new 175m3 stormwater tank. Planned improvement completion date 2035 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13094S | DITCHEAT STORM TANK | 102408 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | MENDIP | Somerton and Frome Co Const | ST6283835114 | GB108052021160 | Alham | RIVER ALHAM |  |  |  |  | Commissioned in 2018 - full year data expected | 57 | 66 | 40 | 81 | 973.75 | 99.9011 | 66.6 | 5 (installed 2018) |  |  | Performance - GW inundation | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2021-05-18 | No sewage litter or sewage fungus | 2021-05-28 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021160 | No | 2022-09-01 | Increase treatment capacity by over 35% from 4.8l/s to 6.5l/s, and storm storage to 52m3. | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Increase treatment capacity by over 35% from 4.8l/s to 6.5l/s, and storm storage to 52m3. Planned improvement completion date 2035 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14227B | STUDLAND WADMORE LANE | 401418 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SZ0298083190 | 250 | Not part of a river WB catchment | TRIBUTARY OF LITTLE SEA |  |  |  |  | Commissioned in 2017 - full year data expected | 3 | 8 | 11 | 12 | 27.5167 | 99.9807 | 6 | 6 (installed 2017) | [13 empty] | Not part of a river WB catchment | No | 2024-12-01 | Network improvements have been made to reduce the storm overflow per year. Surface water separation within with a local development to reduce surface water connections into the sewerage network. | 2025 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Network improvements have been made to reduce the storm overflow per year. Surface water separation within with a local development to reduce surface water connections into the sewerage network. Planned improvement completion date 2025 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13178S | LEIGH ON MENDIP STORM TANK | 010053 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | MENDIP | Somerton and Frome Co Const | ST6992047250 | GB109053022020 | Mells source to conf with Somerset Frome | LEIGH STREAM |  |  |  |  | Commissioned in 2018 - full year data expected | 38 | 31 | 15 | 38 | 296.4667 | 99.7652 | 27 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022020 | No | 2024-03-04 | Provision an additional 28m3 of storm storage via a new in-line storm tank. | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Provision an additional 28m3 of storm storage via a new in-line storm tank. Planned improvement completion date 2045 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13039S | BRUTON GANTS MILL LANE STORM TANK | 102409 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST6724133995 | GB108052021140 | Brue - Upper | RIVER BRUE |  |  |  |  | Commissioned in 2017 - full year data expected | 24 | 17 | 1 | 15 | 142.2366 | 99.9906 | 15.8333 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021140 | No | 2023-03-31 | Provision of 130m3 of additional storm water storage to increase total storm storage to 295m3. | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Provision of 130m3 of additional storm water storage to increase total storm storage to 295m3. Planned improvement completion date 2050 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17543C | BATH LAMBRIDGE RUGBY GROUND CARPARK | 010954 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7634366424 | GB109053022300 | Lam Bk - source to conf R Avon (Brist) | LAM BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 52 | 40 | 32 | 49 | 53.4333 | 99.567 | 43.6 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP or Green Recovery | 2021-03-29 | Sewage litter present, no sewage fungus |  | N/A | 2022-03-01 | Water Quality Modelling shows that the WFD Status Class at the 99%ile level for BOD and Ammonia is High ‘with’ or ‘without’ all Bath FSOs |  | Multiple overflows so unsuitable for invertebrate assessment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022300 | No | 2023-09-28 | Provision of 14.5m3 storm storage & FFT controlled to 6.5l/s to less than 20 spills / year. | 2024 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Provision of 14.5m3 storm storage & FFT controlled to 6.5l/s to less than 20 spills / year. Planned improvement completion date 2024 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13100C | DOYNTON INLET | 102816 | Inlet SO at WwTW |  | Diluted and partially treated | Groundwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST7141373915 | GB109053027510 | Boyd - source to conf R Avon (Brist) | RIVER BOYD (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 56 | 87 | 77 | 108 | 2297.4833 | 98.1893 | 82 | 5 (installed 2018) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [5 empty] | 2022-05-23 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027510 | No | 2023-03-31 | Provision of an additional 27m3 stormwater storage tank. | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Provision of an additional 27m3 stormwater storage tank. Planned improvement completion date 2040 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13199S | MARNHULL COMMON STORM TANK | 040628 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | NORTH DORSET | North Dorset Co Const | ST7645017860 | GB108043016170 | Stour (Upper) | RIVER STOUR |  |  |  |  | Commissioned in 2017 - full year data expected | 113 | 87 | 76 | 122 | 2259.4667 | 100 | 102.8333 | 6 (installed 2017) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2020-04-09 | No sewage litter or sewage fungus | 2020-04-09 | Lab assessment - No impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016170 | No | 2022-06-01 | Provision of an additional 478m3 of storm storage, involving conversion of the one of the existing old sludge tanks. | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Provision of an additional 478m3 of storm storage, involving conversion of the one of the existing old sludge tanks. Planned improvement completion date 2040 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15486B | WEST BEXINGTON | 041125 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | WEST DORSET | West Dorset Co Const | SY5295086620 | GB620806560000 | Lyme Bay East | CHESIL BEACH |  |  |  |  | Commissioned in 2017 - full year data expected | 66 | 87 | 46 | 86 | 678.6834 | 99.0948 | 74.6667 | 6 (installed 2017) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP or Green Recovery | 2018-02-27 | No sewage litter or sewage fungus | 2021-03-10 | Inaccessible | 2021-11-17 | Baseline data, SO not discharging when sampled |  | Outfall in reedbed - cannot always be accessed | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620806560000 | No | 2023-11-01 | Pumping station improvement works complete, further surface water separation and sewer sealing works planned for 2024 to further reduce storm water spills. | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Pumping station improvement works complete, further surface water separation and sewer sealing works planned for 2024 to further reduce storm water spills. Planned improvement completion date 2023 or before - Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14328Z | HANGING LANGFORD | NPSWQD003662 | Storm discharge at pumping station - with treatment | Reed bed | Fully treated | Groundwater | SALISBURY | Salisbury Co Const | SU0449037130 | GB108043022550 | Wylye (Middle) | RIVER WYLYE VIA A REED BED |  |  |  |  | Commissioned in 2019 - full year data expected | 346 | 337 | 188 | 170 | 560.4131 | 99.981 | 280.2 | 4 (installed 2019) |  |  | Performance - GW inundation | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2023-10-19 | No sewage litter or sewage fungus | 2022-01-28 | Lab assessment - No impact | 2022-01-28 | Impact (US 0.16mg/l, DS 0.18mg/l) | See case study page | Has wetland treatment. See case study page. | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022550 | No | 2012-12-01 | Reed beds were constructed in 2012. | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Reed beds were constructed in 2012. Planned improvement completion date 2023 or before - Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15648B | PORTLAND BILL | 402219 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6777068280 | GB620705550000 | Dorset / Hampshire | ENGLISH CHANNEL(C) | PORTLAND NORTH EASTERN BREAKWATER |  |  |  | Commissioned in 2016 - full year data expected | 58 | 46 | 38 | 8 | 6.9667 | 98.2355 | 51.5 | 7 (installed 2016) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP or Green Recovery | 2021-03-16 | Sewage litter present, no sewage fungus |  | N/A |  |  |  | Sea outfall - inverts not suitable | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620705550000 | No | 2022-11-01 | Removed c8,000m2 of impermeable area from the combined sewer, and construct 18m3 of new storage to reduce the storm overflow discharge from over 60/year to c4/year. | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Removed c8,000m2 of impermeable area from the combined sewer, and construct 18m3 of new storage to reduce the storm overflow discharge from over 60/year to c4/year. Planned improvement completion date 2023 or before - Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15167B | CROMHALL JUBILEE LANE | 103286 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6942089520 | GB109054026590 | Tortworth Bk - source to conf R LIttle Avon | THE DYER'S BRAKE(S) |  |  |  |  | Commissioned in 2020 - full year data expected | 117 | 69 | 63 | 137 | 1146.4003 | 100 | 96.5 | 3 (installed 2020) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2023-03-21 | Sewage litter and sewage fungus found | 2022-10-27 | TBC | 2021-12-16 | Baseline data, SO not discharging when sampled |  | Overgrown watercourse | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026590 | No | 2024-03-31 | Seal sewer pipes in Cromhall to prevent groundwater entering the system. | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Seal sewer pipes in Cromhall to prevent groundwater entering the system. Planned improvement completion date 2040 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14302B | IDMISTON | 401574 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SALISBURY | Salisbury Co Const | SU1965637579 | GB108043022390 | Bourne (Hampshire Avon) | RIVER BOURNE (S) |  |  |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 0 | 1 | 0.36667 | 99.9901 | 0.25 | 4 (installed 2019) | [9 empty] | 2022-12-29 | No impact (US 0.08mg/l, DS 0.07mg/l) |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022390 | No | 2024-03-31 | Seal sewer pipes in Idmiston to prevent groundwater entering the system. | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Seal sewer pipes in Idmiston to prevent groundwater entering the system. Planned improvement completion date 2023 or before - Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13282B | SPARKFORD OFF SPARKFORD HILL LANE INLET | 072344 | Inlet SO at WwTW |  | Diluted | A combination of rainwater and groundwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST6050525063 | GB108052015650 | Cam - Lower | THE RIVER CAM |  |  |  |  | Commissioned in 2019 - full year data expected | 81 | 62 | 74 | 151 | 1346.25 | 99.6593 | 73.6 | 4 (installed 2019) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2023-10-20 | No sewage litter or sewage fungus | 2023-10-20 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015650 | No | 2023-11-30 | Site investigations complete, sampling underway to review grass plot performance for future optimisation. | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Site investigations complete, sampling underway to review grass plot performance for future optimisation. Planned improvement completion date 2035 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13212S | MILBORNE ST ANDREW STORM TANK | 042116 | Storm tank at WwTW - with treatment | Reed bed | Fully treated | Groundwater | NORTH DORSET | North Dorset Co Const | SY8025096490 | GB108044009630 | Bere Stream | BERE STREAM(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 12 | 57 | 2 | 46 | 1028.3833 | 99.9998 | 23.4 | 5 (installed 2018) | [9 empty] | 2022-06-28 | Baseline data, SO not discharging when sampled |  | Has wetland treatment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009630 | No | 2024-03-31 | Storm overflow grass plot refurbished (May-24), a new nature based solution is planned for delivery in by 2030. | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Storm overflow grass plot refurbished (May-24), a new nature based solution is planned for delivery in by 2030. Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13303S | SYDLING ST NICHOLAS NEAR HUISH FARM STORM TANK | 401025 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | WEST DORSET | West Dorset Co Const | SY6320198437 | GB108044009700 | Sydling Water | SYDLING WATER |  |  |  |  | Commissioned in 2018 - full year data expected | 142 | 95 | 55 | 134 | 3044.3333 | 100 | 102 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2020-10-26 | Sewage fungus present no sewage litter | 2020-10-26 | Lab assessment - No impact |  |  |  | Sewage fungus at outfall | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009700 | No | 2024-03-31 | Storm overflow grass plot refurbished (May-24), a new nature based solution is planned for delivery in by 2030. | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Storm overflow grass plot refurbished (May-24), a new nature based solution is planned for delivery in by 2030. Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13021S | BISHOPS CAUNDLE BLIND LANE OFF A3030 STORM TANK | 401961 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | WEST DORSET | West Dorset Co Const | ST7038012600 | GB108043015960 | Caundle Brook (Lower) | CAUNDLE BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 37 | 17 | 45 | 74 | 1484.5167 | 99.9854 | 39.6 | 4 (installed 2019) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2023-05-16 | No sewage litter or sewage fungus |  | N/A |  |  |  | Too deep to see outfall | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015960 | No | 2023-11-30 | Storm overflow grass plot refurbished to accommodate storm overflow | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Storm overflow grass plot refurbished to accommodate storm overflow Planned improvement completion date 2035 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13173S | LACOCK STORM TANK | 011342 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | NORTH WILTSHIRE | Chippenham Co Const | ST9195867643 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | BRISTOL AVON |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 35 | 92 | 1536.5333 | 99.9535 | 63.5 | 2 (installed 2021) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No | 2024-03-31 | The treatment capacity of Lacock WRC was more than doubled from 4.8l/s to 9.8l/s. | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - The treatment capacity of Lacock WRC was more than doubled from 4.8l/s to 9.8l/s. Planned improvement completion date 2035 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13057S | CHEDDAR STORM TANK | 071901 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | SEDGEMOOR | Wells Co Const | ST4474352289 | GB109052021540 | Cheddar Yeo - source to conf Stubbingham Rhyne | CHEDDAR YEO |  |  |  |  | Commissioned in 2019 - full year data expected | 80 | 49 | 38 | 77 | 1199.6 | 100 | 57.4 | 4 (installed 2019) |  |  | Performance - GW inundation | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2022-03-31 | Sewage litter present, no sewage fungus | 2022-03-31 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021540 | No | 2023-03-31 | The treatment capacity of the works was increased from 83.5l/s to 94l/s. | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - The treatment capacity of the works was increased from 83.5l/s to 94l/s. Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13075S | COMPTON BASSETT STORM TANK | 102943 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | SU0166070330 | GB109053022050 | Marden - source to conf Cowage Bk | RIVERS BROOK(S) |  |  |  |  | Feb 2023 |  |  |  | 30 | 393.35 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022050 | No | 2023-03-31 | The treatment capacity was increased by nearly 200% (from 17.5l/s to 49l/s). This will require new inlet pumping station and new treatment assets to treat the additional flow. | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - The treatment capacity was increased by nearly 200% (from 17.5l/s to 49l/s). This will require new inlet pumping station and new treatment assets to treat the additional flow. Planned improvement completion date 2040 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13351S | WINSCOMBE STORM TANK | 071977 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | NORTH SOMERSET | Weston-Super-Mare Co Const | ST3999157769 | GB109052021580 | Lox Yeo - source to conf Rive Axe | LOX YEO RIVER |  |  |  |  | Commissioned in 2018 - full year data expected | 101 | 50 | 42 | 111 | 1771.2 | 100 | 74 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2020-03-25 | No sewage litter or sewage fungus | [5 empty] | Unable to locate outfall, investigation ongoing | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021580 | No | 2022-03-01 | Total storm storage was increased to 340m3 by constructing a new stormwater storage tank. | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Total storm storage was increased to 340m3 by constructing a new stormwater storage tank. Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16507C | FROME WESTWAY PRECINCT CAR PARK R/O | 021332 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Somerton and Frome Co Const | ST7764348191 | GB109053022101 | Frome (Maiden Bradley to Mells) | RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 53 | 42 | 22 | 5 | 0.43333 | 100 | 31.25 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP or Green Recovery | 2021-03-09 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022101 | No | 2022-11-01 | Upsize pipes and install new flow controls to reduce discharges to the river Frome from 43/year to c14/year. | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete - Upsize pipes and install new flow controls to reduce discharges to the river Frome from 43/year to c14/year. Planned improvement completion date 2023 or before - Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13255S | RINGWOOD HAMPSHIRE HATCHES LANE STORM TANK | 402536 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | NEW FOREST | New Forest West Co Const | SU1445203396 | GB108043015840 | Hampshire Avon (Lower) | HAMPSHIRE AVON RIVER |  |  |  |  | Commissioned in 2020 - full year data expected |  | 29 | 29 | 109 | 2110.7739 | 99.9959 | 55.6667 | 3 (installed 2020) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2020-11-10 | No sewage litter or sewage fungus | 2021-03-24 | Lab assessment - No impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015840 | No | 2023-12-08 | Increase storm storage to 1,454m3 (existing is 986m3) by constructing a new 470m3 stormwater tank. | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete: Increase storm storage to 1,454m3 (existing is 986m3) by constructing a new 470m3 stormwater tank. Planned improvement completion date 2035 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16897C | BRADFORD-ON-AVON CULVER STREET RECREATION PARK | 101650 | SO on sewer network |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | Chippenham Co Const | ST8223160505 | GB109053027372 | Bristol Avon (Semington Bk to By Bk) | RIVER AVON |  |  |  |  | Commissioned in 2016 - full year data expected | 67 | 61 | 42 | 58 | 237.3217 | 99.8886 | 56.375 | 7 (installed 2016) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP or Green Recovery | 2021-03-16 | No sewage litter or sewage fungus |  | N/A - WQM required | 2022-03-01 | Water Quality Modelling shows no impact |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027372 | No | 2024-01-29 | Provision of 168m3 storm storage to reduce spills to approximately 8 spills / year. | 2024 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete: Provision of 168m3 storm storage to reduce spills to approximately 8 spills / year. Planned improvement completion date 2024 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16462C | BRISTOL HANHAM BEECHWOOD AVENUE | 101753 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6290072190 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON (VIA SWS) |  |  |  |  | Commissioned in 2016 - full year data expected | 78 | 52 | 32 | 38 | 40.7333 | 99.876 | 38.625 | 7 (installed 2016) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Spill reduction scheme - On current WINEP/AMP or Green Recovery | 2021-05-09 | No sewage litter or sewage fungus |  | N/A |  |  |  | No sewage fungus assessment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No | 2024-02-13 | Provision of an additional 50m3 of storage, modify the weir level and fine screen, to reduce discharges from 60/year to 13 events/year. | 2024 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete: Provision of an additional 50m3 of storage, modify the weir level and fine screen, to reduce discharges from 60/year to 13 events/year. Planned improvement completion date 2024 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13132S | GILLINGHAM COMMON MEAD LANE STORM TANK | 401739 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | NORTH DORSET | North Dorset Co Const | ST8065325974 | GB108043022490 | Stour (Headwaters) | RIVER STOUR (UPPER) |  |  |  |  | Commissioned in 2020 - full year data expected | 63 | 58 | 57 | 90 | 827.1333 | 99.903 | 68 | 3 (installed 2020) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2018-03-20 | No sewage litter or sewage fungus | 2018-03-20 | Lab assessment - No impact |  |  |  | RICT analysis also complete (Low) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022490 | No | 2024-03-22 | Provision of an additional 613m3 stormwater storage tank increasing total storage to 1,194m3; 27m3 balance tank also installed. | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete: Provision of an additional 613m3 stormwater storage tank increasing total storage to 1,194m3. ; 27m3 balance tank also installed. Planned improvement completion date 2040 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13258S | SALISBURY PETERSFINGER SOUTHAMPTON ROAD STORM TANK | 401382 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SALISBURY | Salisbury Co Const | SU1690028410 | GB108043015840 | Hampshire Avon (Lower) | RIVER AVON(S) |  |  |  |  | Commissioned in 2020 - full year data expected |  | 14 | 4 | 102 | 1766.6333 | 99.999 | 40 | 3 (installed 2020) |  |  | Performance - Infiltration | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2018-09-11 | No sewage litter or sewage fungus | 2018-09-11 | Lab assessment - No impact |  |  |  | RICT analysis also complete (Moderate) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015840 | No | 2024-03-31 | Seal sewer pipes in Alderbury to prevent groundwater entering the system. | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete: Seal sewer pipes in Alderbury to prevent groundwater entering the system. Planned improvement completion date 2040 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14058B | HORTON FARM, HORTON | 401149 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | KENNET | Devizes Co Const | SU0506063510 | GB108043022430 | Etchilhampton Water | TRIB OF ETCHILHAMPTON WATER(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 167 | 104 | 71 | 162 | 3627.7833 | 100 | 126 | 5 (installed 2018) |  |  | Performance - Infiltration | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2018-11-13 | Sewage litter present, no sewage fungus | Sampled between 2018-2020 | Lab assessment - No impact | 2021-11-16 | Inaccessible at time of visit |  | RICT analysis complete (No Impact) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022430 | No | 2024-03-31 | Seal sewer pipes in Horton to prevent groundwater entering the system. | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete: Seal sewer pipes in Horton to prevent groundwater entering the system. Due for further survey in winter 2024/25. Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17637Z | PIDDLETRENTHIDE ACROSS RIVER FROM RIVENDELL (CSO4) | EPRAP3827XC | SO on sewer network |  | Diluted | Groundwater | WEST DORSET | West Dorset Co Const | ST7027900119 | GB108044010120 | Piddle (Upper) | THE RIVER PIDDLE |  |  |  |  | Commissioned in 2019 - full year data expected | 157 | 132 | 10 | 89 | 2057 | 99.999 | 97 | 4 (installed 2019) |  |  | Performance - Infiltration | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2018-04-20 | No sewage litter or sewage fungus | 2018-03-16 | Lab assessment - No impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010120 | No | 2024-03-31 | Seal sewer pipes throughout the Piddle valley to prevent groundwater entering the system. | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete: Seal sewer pipes throughout the Piddle valley to prevent groundwater entering the system. Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17638Z | PIDDLETRENTHIDE R/O TRENT HOUSE (CSO6) | EPRAP3822XS | SO on sewer network |  | Diluted | Groundwater | WEST DORSET | West Dorset Co Const | SY7048099756 | GB108044010120 | Piddle (Upper) | THE RIVER PIDDLE |  |  |  |  | Commissioned in 2019 - full year data expected | 101 | 62 | 10 | 93 | 2126 | 99.999 | 66.5 | 4 (installed 2019) |  |  | Performance - Infiltration | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2018-04-20 | No sewage litter or sewage fungus | 2018-03-16 | Lab assessment - Impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010120 | No | 2024-03-31 | Seal sewer pipes throughout the Piddle valley to prevent groundwater entering the system. | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete: Seal sewer pipes throughout the Piddle valley to prevent groundwater entering the system. Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13163S | IWERNE MINSTER STORM TANK | 401089 | Storm tank at WwTW |  | Fully treated | Groundwater | NORTH DORSET | North Dorset Co Const | ST8622414055 | GB108043016010 | Iwerne | RIVER IWERNE |  |  |  |  | Commissioned in 2019 - full year data expected | 135 | 69 | 20 | 107 | 2046.3167 | 99.9585 | 71.4 | 4 (installed 2019) |  |  | Performance - Other maintenance / capital works (e.g. jetting) | Resolved - Oct | N/A - Operational solution applied |  |  | 2021-04-03 | Lab assessment - No impact |  |  |  | Has wetland treatment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016010 | No | 2023-07-31 | Storm overflow grass plot refurbished (May-24), a new nature based solution is planned for delivery in by 2030. | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Complete: Storm overflow grass plot refurbished (May-24), a new nature based solution is planned for delivery in by 2030. Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13015S | BARFORD ST MARTIN BURCOMBE STORM TANK | 041560 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | SALISBURY | Salisbury Co Const | SU0604231168 | GB108043022470 | Nadder (Middle) | RIVER NADDER |  |  |  |  | Commissioned in 2019 - full year data expected | 118 | 69 | 10 | 122 | 1680.75 | 99.9287 | 79.75 | 4 (installed 2019) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2023-10-19 | No sewage litter or sewage fungus | 2023-10-19 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022470 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13353S | WISHFORD WILTON ROAD STORM TANK | 041799 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | SALISBURY | Salisbury Co Const | SU0886833771 | GB108043022510 | Wylye (Lower) | RIVER WYLYE |  |  |  |  | Commissioned in 2019 - full year data expected | 37 | 0 | 6 | 122 | 2233 | 99.9715 | 36 | 4 (installed 2019) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022510 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13036S | BROADMAYNE WEST KNIGHTON ROAD STORM TANK | 040725 | Storm tank at WwTW - with treatment | Reed bed | Fully treated | A combination of rainwater and groundwater | WEST DORSET | West Dorset Co Const | SY7341086760 | GB108044009660 | Tadnoll Brook (including Empool Bottom) | TADNOLL BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 77 | 31 | 22 | 91 | 1497 | 99.9893 | 49.3333 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2021-04-27 | No sewage litter or sewage fungus | 2021-04-27 | Lab assessment - No impact |  |  |  | Has wetland treatment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009660 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13042S | BUTCOMBE STORM TANK | 071124 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | NORTH SOMERSET | North Somerset Co Const | ST5013360124 | GB109052021640 | Yeo - source to conf Congresbury Yeo | CONGRESBURY YEO AND BUTCOMBE |  |  |  |  | Commissioned in 2019 - full year data expected | 68 | 31 | 39 | 167 | 3188.8333 | 100 | 67.6 | 4 (installed 2019) |  |  | Performance - Infiltration | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021640 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13129S | FOVANT STORM TANK | 401338 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | SALISBURY | South West Wiltshire Co Const | ST9983330171 | GB108043016190 | Fovant Brook | FOVANT BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 115 | 60 | 58 | 139 | 1707.25 | 99.9617 | 94.4 | 4 (installed 2019) |  |  | Performance - Infiltration | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2020-11-24 | No sewage litter or sewage fungus | 2020-11-24 | Lab assessment - No impact |  |  |  | Sewage fungus present on outfall and downstream (May 2020) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016190 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13346S | WICK ST LAWRENCE STORM TANK | 102350 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | NORTH SOMERSET | Weston-Super-Mare Co Const | ST3651066600 | GB540805210900 | PARRETT | CONGRESBURY YEO(E) |  |  |  |  | Commissioned in 2019 - full year data expected | 137 | 62 | 24 | 107 | 1992.3667 | 96.4411 | 88.4 | 4 (installed 2019) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2022-03-23 | No sewage litter or sewage fungus | 2022-03-23 | TRAC site - N/A |  |  |  | Discharges to side channel, goes underground | https://environment.data.gov.uk/catchment-planning/WaterBody/GB540805210900 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14220B | LYTCHETT MATRAVERS BULBURY LANE | 401452 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | PURBECK | Mid Dorset and North Poole Co Const | SY9370094150 | GB108044010100 | Sherford River | TRIB OF SHERFORD RIVER |  |  |  |  | Commissioned in 2018 - full year data expected | 64 | 44 | 37 | 71 | 738.75 | 99.9839 | 54.5714 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2020-10-13 | Sewage litter present, no sewage fungus | 2020-10-13 | N/A | 2022-02-11 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010100 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13082S | CRANBORNE HIGHER HOLWELL STORM TANK | 040023 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | EAST DORSET | North Dorset Co Const | SU0649013050 | GB108043016090 | Crane (Dorset) | RIVER CRANE (S) |  |  |  |  | Commissioned in 2020 - full year data expected |  | 97 | 3 | 106 | 2287.7 | 99.0793 | 68.6667 | 3 (installed 2020) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue |  |  |  |  | 2022-06-28 | Impact (US 0.33mg/l, DS 0.39mg/l) |  | Combined FE and SO | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016090 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Planned improvement completion date 2030 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13280S | SOUTH PERROTT NEAR PIPPLEPEN FARM STORM TANK | 071228 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | ST4701507400 | GB108052015260 | Parrett - headwaters to Broad River | RIVER PARRETT |  |  |  |  | Commissioned in 2017 - full year data expected | 53 | 29 | 21 | 35 | 209.2333 | 100 | 60.1667 | 6 (installed 2017) |  |  | Performance - Infiltration | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2020-05-01 | No sewage litter or sewage fungus | 2020-05-01 | Lab assessment - No impact |  |  |  | RICT analysis complete (Extremely severe) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015260 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Planned improvement completion date 2035 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19613C | MONTACUTE NR OLD STW | 102265 | SO on sewer network |  | Diluted | Groundwater | SOUTH SOMERSET | Yeovil Co Const | ST4946017760 | GB108052015350 | Wellhams Brook | TRIBUTARY OF WELLAHMS BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 109 | 68 | 37 | 128 | 1836.9667 | 99.3204 | 85.5 | 5 (installed 2018) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015350 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan) | Planned improvement completion date 2040 - Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13025S | BLAGDON STORM TANK | 070005 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | NORTH SOMERSET | Weston-Super-Mare Co Const | ST5008160062 | GB109052021640 | Yeo - source to conf Congresbury Yeo | CONGRESBURY YEO |  |  |  |  | Commissioned in 2019 - full year data expected | 41 | 22 | 26 | 37 | 579.4667 | 99.6948 | 32.4 | 4 (installed 2019) | [5 empty] | 2022-10-11 | No sewage litter or sewage fungus |  | N/A - WQM required |  |  |  | Sewage fungus for 10m downstream | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021640 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13029S | BOX MILL LANE STORM TANK | 010528 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST8235568829 | GB109053027380 | By Bk - conf Doncombe Bk to conf R Avon (Brist) | BY BROOK (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 48 | 50 | 46 | 96 | 1619.5667 | 98.5308 | 59.6 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2021-03-29 | No sewage litter or sewage fungus |  | N/A - WQM required | 2022-08-01 | UPM - RAT Level 1 WQ gives no impact |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027380 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13032C | BRADFORD ON TONE INLET | 070006 | Inlet SO at WwTW |  | Diluted | Groundwater | TAUNTON DEANE | Taunton Deane Co Const | ST1771523485 | GB108052015481 | Tone - Wellington to Taunton | RIVER TONE |  |  |  |  | Commissioned in 2018 - full year data expected | 143 | 103 | 87 | 154 | 1872.0167 | 99.957 | 124.8 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2021-03-23 | Sewage fungus present no sewage litter | [5 empty] | Sewage fungus for 5m downstream | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015481 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13043S | BUTLEIGH STORM TANK | 071978 | Storm tank at WwTW |  | Diluted | Groundwater | MENDIP | Somerton and Frome Co Const | ST5329034570 | GB108052021182 | Brue - Tootle Bridge to Clyse Hole | RIVER BRUE (S) |  |  |  |  | Commissioned in 2020 - full year data expected |  | 134 | 106 | 147 | 2727.3333 | 99.9939 | 129 | 3 (installed 2020) |  |  | Performance - GW inundation | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2018-10-05 | No sewage litter or sewage fungus | 2018-10-05 | Lab assessment - No impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021182 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13056C | CHARMOUTH SEA OUTFALL INLET | 401625 | Inlet SO at WwTW |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | SY3678091710 | GB620806560000 | Lyme Bay East | LYME BAY |  | CHARMOUTH WEST | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=charm&site=ukk2205-21300 |  | Commissioned in 2016 - full year data expected | 69 | 65 | 65 | 101 | 217.6709 | 99.9991 | 67.875 | 7 (installed 2016) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2022-03-17 | No sewage litter or sewage fungus | 2022-03-17 | TRAC site - N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620806560000 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13058S | CHEW STOKE WALLEY COURT ROAD STORM TANK | 102937 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST5704762083 | GB109053021852 | Chew - Chew Valley Lake to conf Winford Brook | RIVER CHEW |  |  |  |  | Commissioned in 2018 - full year data expected | 202 | 140 | 101 | 187 | 3572.1 | 99.8828 | 126 | 5 (installed 2018) |  |  | Performance - Infiltration | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2023-10-02 | No sewage litter but sewage fungus found d/s and in the mixing zone | 2023-10-02 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021852 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13060S | CHIDEOCK MILL LANE STORM TANK | 401068 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | WEST DORSET | West Dorset Co Const | SY4254092240 | 267 | Not part of a river WB catchment | RIVER WINNIFORD(S) |  | SEATOWN | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=seatow&site=ukk2205-21200 |  | Commissioned in 2016 - full year data expected | 77 | 62 | 35 | 60 | 842.5 | 100 | 56.375 | 7 (installed 2016) |  |  | Performance - GW inundation | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | [8 empty] | Not part of a river WB catchment | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13077S | CORFE CASTLE WYTCH FARM ROAD STORM TANK | 041324 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | PURBECK | South Dorset Co Const | SY9609683153 | GB108044010020 | Corfe River | CORFE RIVER (S) | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA |  |  |  | Commissioned in 2016 - full year data expected | 44 | 22 | 22 | 60 | 631.5666 | 98.5506 | 26.875 | 7 (installed 2016) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010020 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13095S | DONYATT OFF A358 STORM TANK | 102390 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST3404714243 | GB108052015190 | Isle - Upper to conf Cad Bk | RIVER ISLE |  |  |  |  | Commissioned in 2018 - full year data expected | 23 | 18 | 13 | 29 | 123.8333 | 99.8988 | 22.4 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015190 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13099S | DOWNTON MOOT LANE STORM TANK | 041354 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | SALISBURY | Salisbury Co Const | SU1741420421 | GB108043015840 | Hampshire Avon (Lower) | HAMPSHIRE AVON, RIVER |  |  |  |  | Commissioned in 2020 - full year data expected |  | 35 | 26 | 106 | 1231.4333 | 100 | 55.6667 | 3 (installed 2020) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2017-09-25 |  | 2017-09-25 | Inaccessible |  |  |  | Visited site - unable to collect data | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015840 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13120S | EVERSHOT OFF EAST HILL STORM TANK | 042453 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | WEST DORSET | West Dorset Co Const | ST5781104386 | GB108044009620 | Frome Dorset (Headwaters) | RIVER FROME |  |  |  |  | Commissioned in 2017 - full year data expected | 66 | 43 | 36 | 79 | 711.5333 | 99.977 | 49.6667 | 6 (installed 2017) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2022-07-20 | No sewage litter or sewage fungus |  | N/A | 2022-04-13 | No impact |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009620 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13128S | FORDINGBRIDGE FROG LANE STORM TANK | 401342 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | NEW FOREST | New Forest West Co Const | SU1465213085 | GB108043015840 | Hampshire Avon (Lower) | HAMPSHIRE AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 100 | 31 | 19 | 52 | 197.0667 | 100 | 50.4 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2023-11-24 | No sewage litter or sewage fungus | 2023-11-24 | TBC | 2022-02-07 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015840 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13137S | GREAT SOMERFORD STORM TANK | 102840 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9647083213 | GB109053027650 | Avon (Brist) conf Tetbury Avon to conf R Marden | RIVER AVON(S) |  |  |  |  | Commissioned in 2020 - full year data expected |  | 35 | 27 | 73 | 771.4431 | 99.9832 | 45 | 3 (installed 2020) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027650 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13161S | ILMINSTER ASHWELL STORM TANK | 102395 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | SOUTH SOMERSET | Yeovil Co Const | ST3559016190 | GB108052015190 | Isle - Upper to conf Cad Bk | RIVER ISLE |  |  |  |  | Commissioned in 2017 - full year data expected | 58 | 47 | 44 | 83 | 1108.25 | 99.9735 | 50.5 | 6 (installed 2017) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2023-03-10 | Not visible - too deep | 2023-03-10 | Too deep to get samples |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015190 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13168Z | KILVE BEACH CAR PARK STORM TANK | 102917 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | ST1422144659 | GB670807410000 | Bridgwater Bay | BRISTOL CHANNEL (COASTAL) |  |  |  |  | Commissioned in 2019 - full year data expected | 82 | 37 | 26 | 72 | 1149.5 | 99.9092 | 51.6 | 4 (installed 2019) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2020-11-26 |  | 2020-11-26 | Inaccessible |  |  |  | Not a suitable site for lone working | https://environment.data.gov.uk/catchment-planning/WaterBody/GB670807410000 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13172S | KINSON NEW ROAD NORTHBOURNE STORM TANK | 401495 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | BOURNEMOUTH | Bournemouth West Boro Const | SZ0879096520 | GB108043011040 | Stour (Lower) | LOWER RIVER STOUR(S) |  | CHRISTCHURCH AVON BEACH/CHRISTCHURCH FRIAR'S CLIFF | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=avon%20b&site=ukk2201-18800 | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=friar&site=ukk2201-18750 | Commissioned in 2016 - full year data expected | 14 | 8 | 17 | 47 | 570.5779 | 99.9999 | 21.125 | 7 (installed 2016) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2018-09-05 | No sewage litter or sewage fungus | 2018-09-05 | Lab assessment - No impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011040 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13176C | LANGTON HERRING OFF LOWER FARM INLET | 040049 | Inlet SO at WwTW |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | SY6093382762 | 2 | Not part of a river WB catchment | TRIBUTARY OF WEST FLEET |  |  |  |  | Commissioned in 2020 - full year data expected | 7 | 13 | 14 | 28 | 59.5 | 99.8954 | 15.5 | 3 (installed 2020) | [13 empty] | Not part of a river WB catchment | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13190S | LYTCHETT MINSTER LYTCHETT BAY STORM TANK | 401242 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | PURBECK | Mid Dorset and North Poole Co Const | SY9685092300 | GB520804415800 | POOLE HARBOUR | LYTCHETT BAY(E) | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA | POOLE HARBOUR ROCKLEY SANDS | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=rockl&site=ukk2102-19450 |  | Commissioned in 2016 - full year data expected | 23 | 18 | 17 | 29 | 399.2802 | 99.9714 | 12.25 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB520804415800 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13191C | MAIDEN BRADLEY INLET | 400608 | Inlet SO at WwTW - with treatment | Reed bed | Fully treated | Rainwater | SALISBURY | South West Wiltshire Co Const | ST8106038540 | GB108043022520 | Wylye (Headwaters) | GROUNDWATER VIA INFILT SYSTEM |  |  |  |  | Commissioned in 2019 - full year data expected | 67 | 74 | 67 | 91 | 195.25 | 99.9851 | 69.6 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | [7 empty] | Has wetland treatment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022520 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13193S | MALMESBURY STORM TANK | 102361 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9432386909 | GB109053027650 | Avon (Brist) conf Tetbury Avon to conf R Marden | RIVER AVON |  |  |  |  | Commissioned in 2019 - full year data expected | 77 | 41 | 45 | 93 | 1192.7167 | 100 | 62 | 4 (installed 2019) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2020-10-16 | No sewage litter or sewage fungus | [6 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027650 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13202S | MEARE STORM TANK | EPRMP3728GG | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | MENDIP | Wells Co Const | ST4509941737 | GB108052021190 | Brue - Clyce Hole to conf North Drain | TRIBUTARY OF THE RIVER BRUE |  |  |  |  | Commissioned in 2020 - full year data expected |  | 91 | 59 | 91 | 1344.9 | 100 | 80.3333 | 3 (installed 2020) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021190 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13207S | MERE ROOK STREET STORM TANK | 040059 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | SALISBURY | South West Wiltshire Co Const | ST8127331578 | GB108043022450 | Shreen Water (including Ashfield Water) | SHREEN WATER |  |  |  |  | Commissioned in 2018 - full year data expected | 33 | 20 | 18 | 53 | 381.7 | 99.9026 | 30.4 | 5 (installed 2018) | [5 empty] | 2023-09-27 | No sewage litter or sewage fungus | 2023-09-27 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022450 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13215S | MINEHEAD HEADWORKS STORM TANK | 100386 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | SS9945046970 | GB640807670000 | Bristol Channel Inner South | (C) BRISTOL CHANNEL |  | MINEHEAD TERMINUS | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=mineh&site=ukk2305-35000 |  | Commissioned in 2016 - full year data expected | 62 | 35 | 23 | 63 | 459.0631 | 99.8682 | 33.875 | 7 (installed 2016) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2023-10-11 | TRAC site - N/A |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB640807670000 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13243C | PORTBURY WHARF THE DROVE PORTBURY INLET | 100385 | Inlet SO at WwTW |  | Diluted | A combination of rainwater and groundwater | NORTH SOMERSET | North Somerset Co Const | ST4855078150 | GB530905415405 | BRISTOL AVON | (E) SEVERN ESTUARY |  |  |  |  | Commissioned in 2019 - full year data expected | 177 | 108 | 95 | 180 | 1993.5 | 100 | 127.2 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2022-10-10 | No sewage litter or sewage fungus | 2022-10-10 | TRAC site - N/A |  |  |  | Inaccessible sea outfall | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13250S | PUNCKNOWLE NEXT TO GULLY KNAP FARM STORM TANK | 042618 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | WEST DORSET | West Dorset Co Const | SY5345989626 | GB108044009550 | Bride | RIVER BRIDE |  |  |  |  | Commissioned in 2019 - full year data expected | 13 | 35 | 46 | 92 | 1742.7187 | 99.7158 | 46.5 | 4 (installed 2019) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009550 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13324S | WAREHAM KEYSWORTH DRIVE STORM TANK | 401336 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | PURBECK | Mid Dorset and North Poole Co Const | SY9364388640 | GB520804415800 | POOLE HARBOUR | TIDAL RIVER PIDDLE | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA | POOLE HARBOUR ROCKLEY SANDS | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=rockl&site=ukk2102-19450 |  | Commissioned in 2016 - full year data expected | 30 | 6 | 10 | 27 | 105.1757 | 99.9935 | 18.25 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB520804415800 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13330S | WELLINGTON TONE STORM TANK | 101332 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST1305422012 | GB108052015481 | Tone - Wellington to Taunton | TRIBUTARY OF RIVER TONE |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 26 | 48 | 361.1 | 99.9737 | 37 | 1 (installed 2022) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2018-05-04 | No sewage litter or sewage fungus | [6 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015481 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13340C | WESTON-SUPER-MARE BLACK ROCK WINDWHISTLE ROAD | 101579 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH SOMERSET | Weston-Super-Mare Co Const | ST3058058690 | GB540805210900 | PARRETT | AXE ESTUARY(E) |  | WESTON-SUPER-MARE UPHILL SLIPWAY/WESTON MAIN | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=weston&site=ukk1202-35700 | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=weston&site=ukk1202-35800 | Commissioned in 2016 - full year data expected | 21 | 12 | 8 | 26 | 174.2742 | 100 | 14.375 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB540805210900 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13515Z | PORLOCK SPARKHAYES LANE STORM TANK | 100318 | Storm tank at WwTW |  | Diluted | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | SS8835048300 | GB108051020300 | Hawcombe STR | PORLOCK BAY HAWKCOMBESTREAM(C) |  | PORLOCK WEIR | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=porlo&site=ukk2305-34900 |  | Commissioned in 2016 - full year data expected | 47 | 13 | 11 | 34 | 602.2333 | 99.9998 | 33.75 | 7 (installed 2016) | [5 empty] | 2020-11-12 | No sewage litter or sewage fungus | 2020-11-12 | Lab assessment - No impact |  |  |  | RICT analysis complete (No Impact) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108051020300 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14110B | STOKE ST MICHAEL STOKE HILL | 102699 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | MENDIP | Somerton and Frome Co Const | ST6665747152 | GB109053022020 | Mells source to conf with Somerset Frome | TRIB OF MELLS STREAM |  |  |  |  | Commissioned in 2019 - full year data expected | 22 | 11 | 1 | 1 | 3.25 | 94.9924 | 8.75 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022020 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14113B | TRUDOXHILL | 102700 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Somerton and Frome Co Const | ST7511043708 | GB109053022080 | Frome - source to conf Maiden Bradley Bk | TRIBUTARY OF RIVER FROME |  |  |  |  | Commissioned in 2019 - full year data expected | 61 | 33 | 40 | 65 | 612.7 | 99.8116 | 49.6 | 4 (installed 2019) |  |  | Performance - Pump failure / issue | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2021-05-18 | No sewage litter or sewage fungus | 2021-05-18 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022080 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14216B | STOBOROUGH KINGS ARMS | 401198 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SY9240086500 | GB108044009692 | Frome Dorset (Lower) d/s Louds Mill Dorchester | TRIB OF RIVER FROME (S) |  |  |  |  | Commissioned in 2016 - full year data expected | 9 | 11 | 13 | 25 | 156.55 | 99.9775 | 12.8571 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009692 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14222B | EAST KNIGHTON BLACKNOLL | 401166 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SY8100086050 | GB108044009650 | Frome Dorset Trib (River Win) | RIVER WIN (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 11 | 13 | 15 | 22 | 73.6164 | 99.9998 | 15.25 | 5 (installed 2018) | [9 empty] | 2021-10-13 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009650 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14244B | SWANAGE DURLSTON ROAD | 402252 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SZ0337077980 | 250 | Not part of a river WB catchment | UNNAMED STREAM TO DURLSTON BAY |  |  |  |  | Commissioned in 2018 - full year data expected | 73 | 53 | 33 | 43 | 66.2833 | 100 | 50.5 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2023-10-17 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | Not part of a river WB catchment | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14252B | STUDLAND COOMBE | 401199 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SZ0346082780 | GB620705550000 | Dorset / Hampshire | STUDLAND BAY(C) |  | STUDLAND KNOLL HOUSE | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=studl&site=ukk2204-19700 |  | Commissioned in 2016 - full year data expected | 9 | 2 | 2 | 8 | 6.3333 | 99.8734 | 14.25 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620705550000 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14261B | STUDLAND WATERY LANE | 041159 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SZ0387182448 | 250 | Not part of a river WB catchment | TRIBUTARY OF STUDLAND BAY |  |  |  |  | Commissioned in 2017 - full year data expected | 19 | 6 | 9 | 1 | 8.4667 | 99.9996 | 8.1667 | 6 (installed 2017) | [13 empty] | Not part of a river WB catchment | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14265B | UPTON MOORLANDS WAY | 401241 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | Mid Dorset and North Poole Co Const | SY9757092640 | GB520804415800 | POOLE HARBOUR | LYTCHETT BAY(C) | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA | POOLE HARBOUR ROCKLEY SANDS | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=rockl&site=ukk2102-19450 |  | Commissioned in 2016 - full year data expected | 26 | 16 | 19 | 35 | 228.4556 | 99.9971 | 27.375 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB520804415800 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14273B | WOOL RAILWAY COTTAGES | 401164 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SY8430086970 | GB108044009692 | Frome Dorset (Lower) d/s Louds Mill Dorchester | TRIB OF RIVER FROME(S) |  |  |  |  | Commissioned in 2020 - full year data expected | 18 | 13 | 8 | 38 | 51.221 | 100 | 19.25 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009692 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14311B | TILSHEAD CAMP ROAD | 401790 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | SALISBURY | Salisbury Co Const | SU0353047810 | GB108043022570 | Till (Hampshire Avon) | RIVER TILL |  |  |  |  | Commissioned in 2017 - full year data expected | 92 | 24 | 0 | 37 | 774.3333 | 99.4673 | 38.25 | 6 (installed 2017) | [5 empty] | 2022-10-03 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022570 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14413B | CHIDEOCK SEATOWN | 043190 | Storm discharge at pumping station |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | SY4208091780 | 267 | Not part of a river WB catchment | WINNIFORD (S) |  | SEATOWN | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=seatow&site=ukk2205-21200 |  | Commissioned in 2016 - full year data expected | 14 | 6 | 4 | 15 | 67 | 99.9575 | 10 | 7 (installed 2016) | [9 empty] | 2021-10-14 | Baseline data, SO not discharging when sampled |  |  | Not part of a river WB catchment | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14415B | LITTON CHENEY CHICKSBRIDGE | 401592 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | WEST DORSET | West Dorset Co Const | SY5407089720 | GB108044009550 | Bride | RIVER BRIDE(S) |  |  |  |  | Commissioned in 2019 - full year data expected | 170 | 113 | 89 | 184 | 3671.9606 | 99.7997 | 139 | 4 (installed 2019) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2023-05-02 | No sewage litter or sewage fungus | 2023-05-02 | TBC | 2021-10-14 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009550 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14439B | WARMINSTER CALVESWATER | 401094 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8814044220 | GB108043022540 | Wylye Trib (The Were or Swan) | THE WERE VIA SWS |  |  |  |  | Commissioned in 2017 - full year data expected | 18 | 24 | 26 | 45 | 141.5833 | 99.9838 | 30.3333 | 6 (installed 2017) | [5 empty] | 2023-10-19 | No sewage litter or sewage fungus | 2023-10-19 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022540 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14583B | BRISTOL WEST TOWN ROAD | 102067 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol North West Boro Const | ST5202277004 | GB530905415405 | BRISTOL AVON | RIVER AVON (ESTUARINE) |  |  |  |  | Commissioned in 2019 - full year data expected | 55 | 26 | 15 | 29 | 55.4167 | 99.9667 | 31.25 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14588B | WEST LULWORTH LULWORTH OUTFALL PS | 401864 | Storm discharge at pumping station |  | Diluted | A combination of rainwater and groundwater | PURBECK | South Dorset Co Const | SY8242079730 | GB620705550000 | Dorset / Hampshire | ENGLISH CHANNEL(C) |  | LULWORTH COVE | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=lulw&site=ukk2204-20000 |  | Commissioned in 2016 - full year data expected | 61 | 15 | 8 | 11 | 2.6833 | 92.9777 | 20.5 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620705550000 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15002B | BOSCOMBE NO 1 | 400551 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BOURNEMOUTH | Bournemouth East Boro Const | SZ1143090450 | GB620705550000 | Dorset / Hampshire | POOLE BAY (C) |  | BOURNEMOUTH BOSCOMBE PIER | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=bournem&site=ukk2101-19060 |  | Commissioned in 2016 - full year data expected | 6 | 11 | 7 | 11 | 6.7909 | 100 | 13.5 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620705550000 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15007B | BOURNEMOUTH IFORD LANE TUCKTON | 401244 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BOURNEMOUTH | Bournemouth East Boro Const | SZ1466092520 | 66 | Not part of a river WB catchment | RIVER STOUR(S) |  | CHRISTCHURCH AVON BEACH/CHRISTCHURCH FRIAR'S CLIFF | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=avon%20b&site=ukk2201-18800 | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=friar&site=ukk2201-18750 | Commissioned in 2016 - full year data expected | 14 | 11 | 8 | 14 | 29.95 | 99.641 | 11 | 7 (installed 2016) | [13 empty] | Not part of a river WB catchment | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15051B | CORFE MULLEN RUSHCOMBE BOTTOM | 401393 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | EAST DORSET | Mid Dorset and North Poole Co Const | SY9938097180 | GB108043016052 | Stour (Middle d/s Pimperne Brook) | RUSHCOMBE STREAM |  |  |  |  | Commissioned in 2018 - full year data expected | 21 | 18 | 26 | 30 | 90.2967 | 99.9517 | 23.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016052 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15052B | VERWOOD EBBLAKE | 400643 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | EAST DORSET | North Dorset Co Const | SU1079607805 | GB108043016090 | Crane (Dorset) | (S) EBBLAKE STREAM |  |  |  |  | Commissioned in 2017 - full year data expected | 30 | 15 | 15 | 22 | 290.3667 | 99.9998 | 17.1667 | 6 (installed 2017) | [5 empty] | 2023-11-24 | No sewage litter or sewage fungus | 2023-11-24 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016090 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15235B | POOLE SHORE ROAD | 051290 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | POOLE | Poole Boro Const | SZ0547787983 | GB620705550000 | Dorset / Hampshire | ENGLISH CHANNEL |  | POOLE SHORE ROAD BEACH | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=shore%20ro&site=ukk2102-19200 |  | Commissioned in 2016 - full year data expected | 53 | 26 | 28 | 45 | 234.5851 | 99.9121 | 40 | 7 (installed 2016) |  |  | Performance - Pump failure / issue | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2022-09-28 | No sewage litter or sewage fungus | 2022-09-28 | TRAC site - N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620705550000 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15278B | LONG SUTTON BENNETTS ORCHARD | 102399 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST4666725386 | GB108052021150 | King's Sedgemoor Drain - Henley Sluice to mouth | CROUDS LAKE |  |  |  |  | Commissioned in 2019 - full year data expected | 64 | 57 | 48 | 79 | 1597.5833 | 99.8891 | 59.4 | 4 (installed 2019) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue |  |  | 2019-11-29 | Lab assessment - Impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021150 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15316B | BARTON ST DAVID TOOTLE BRIDGE | 103177 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST5507932658 | GB108052021182 | Brue - Tootle Bridge to Clyse Hole | TRIBUTARY OF CUNLEASE RHYNE |  |  |  |  | Commissioned in 2019 - full year data expected | 95 | 70 | 90 | 119 | 2271.6 | 99.7019 | 82.6 | 4 (installed 2019) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2020-10-22 | Sewage litter present, no sewage fungus | 2020-10-22 | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021182 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15435B | BATHPOOL HYDE LANE | 103186 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST2538025560 | GB108052015482 | Tone Ds Taunton | RIVER TONE |  |  |  |  | Commissioned in 2019 - full year data expected | 29 | 42 | 22 | 47 | 333.5497 | 99.9247 | 38.5 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2018-10-16 | Sewage litter present, no sewage fungus | 2018-10-16 | Lab assessment - No impact |  |  |  | RICT analysis complete (No Impact) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015482 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15440B | NORTH CURRY MAIN | 101806 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST3200025980 | 200 | Not part of a river WB catchment | TRIB OF RIVER TONE (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 31 | 21 | 18 | 16 | 38 | 99.5748 | 21.5 | 5 (installed 2018) | [9 empty] | 2022-01-17 | Baseline data, SO not discharging when sampled |  |  | Not part of a river WB catchment | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15516B | BILBROOK | 101656 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | ST0325041420 | GB108051020390 | Pill | PILL RIVER (S) |  | BLUE ANCHOR WEST | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=blue%20a&site=ukk2305-35200 |  | Commissioned in 2016 - full year data expected | 26 | 35 | 23 | 36 | 208.3633 | 99.9604 | 26.375 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108051020390 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15552B | WEYMOUTH KNIGHTSDALE NEWSTEAD ROAD | 400892 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6758078730 | GB510804415700 | WEY | WEYMOUTH HARBOUR(E) |  |  |  |  | Oct 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [5 empty] | 2023-10-05 | Sea outfall - N/A |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB510804415700 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15580B | LANGFORD BLACKMOOR ROAD | 012883 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | NORTH SOMERSET | Weston-Super-Mare Co Const | ST4635061120 | GB109052021640 | Yeo - source to conf Congresbury Yeo | LANGFORD BROOK (S) |  |  |  |  | Commissioned in 2020 - full year data expected | 33 | 20 | 10 | 60 | 1039 | 99.8842 | 30.75 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021640 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15621B | CLEVEDON LADYE BAY | 102489 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH SOMERSET | North Somerset Co Const | ST4074072820 | GB530905415405 | BRISTOL AVON | BRISTOL CHANNEL (E) |  | CLEVEDON BEACH | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=cleved&site=ukk1202-36000 |  | Commissioned in 2016 - full year data expected | 41 | 38 | 26 | 36 | 57.3589 | 99.9998 | 34.125 | 7 (installed 2016) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2022-10-10 | No sewage litter or sewage fungus |  | N/A |  |  |  | Outfall too far into estuary | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15673B | PORTLAND SOUTHWELL | 040686 | Storm discharge at pumping station |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6908069880 | GB620705550000 | Dorset / Hampshire | FRESHWATER BAY | PORTLAND NORTH EASTERN BREAKWATER |  |  |  | Commissioned in 2016 - full year data expected | 8 | 18 | 10 | 19 | 23.7833 | 99.9996 | 11.75 | 7 (installed 2016) | [5 empty] | 2023-10-11 | Sea outfall - N/A |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620705550000 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16197C | BRISTOL HOTWELLS ROAD EAST | 102900 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5769572507 | GB530905415405 | BRISTOL AVON | FLOATING HARBOUR |  |  |  |  | Commissioned in 2018 - full year data expected | 10 | 19 | 12 | 14 | 7.7667 | 99.9992 | 11.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16302C | STON EASTON WELLOW BROOK IN FIELD NEAR BY | 013134 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Wells Co Const | ST6295053940 | GB109053022250 | Wellow Bk - source to conf Snails Bk | WELLOW BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 64 | 42 | 49 | 88 | 171.2 | 95.8044 | 46.1667 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2023-11-16 | No sewage litter or sewage fungus | 2023-11-16 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022250 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16342C | BRISTOL ST GEORGES PARK SOUTH 28 LYNDALE ROAD | 102883 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST5612074460 | GB530905415405 | BRISTOL AVON | RIVER AVON (ESTUARINE) |  |  |  |  | Commissioned in 2019 - full year data expected | 37 | 35 | 23 | 43 | 41.6667 | 99.9916 | 34.4 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16365C | BRISTOL ABBEY ROAD O/S NO 123 | 013103 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5673777541 | GB109053027530 | Trym - source to conf R Avon (Brist) | RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 24 | 27 | 22 | 32 | 15.6667 | 100 | 26.25 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16367C | BRISTOL CANFORD ROAD / CANFORD LANE | 013105 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5673777541 | GB109053027530 | Trym - source to conf R Avon (Brist) | RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 10 | 15 | 13 | 24 | 15.5 | 100 | 11.8333 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16378C | BRISTOL HENLEAZE ROAD OPP 1 PYCROFT AVE | 100473 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5801977357 | GB109053027530 | Trym - source to conf R Avon (Brist) | TRIB OF RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2021 - full year data expected |  | 16 | 17 | 20 | 6 | 99.7295 | 17.6667 | 2 (installed 2021) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16379C | BRISTOL HENLEAZE ROAD O/S EASTFIELD INN | 100479 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5801977358 | GB109053027530 | Trym - source to conf R Avon (Brist) | TRIB OF RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 36 | 36 | 34 | 49 | 39.9 | 94.5019 | 38.75 | 5 (installed 2018) | [5 empty] | 2023-09-25 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16381C | BRISTOL HIGH STREET / HENBURY ROAD | 101829 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5721077510 | GB109053027530 | Trym - source to conf R Avon (Brist) | RIVER AVON (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 48 | 39 | 37 | 53 | 141.45 | 99.9671 | 44.25 | 5 (installed 2018) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2023-09-25 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16384C | BRISTOL NEWCOMBE ROAD O/S NO 11 | 013102 | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol North West Boro Const | ST5673777541 | GB109053027530 | Trym - source to conf R Avon (Brist) | RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 16 | 42 | 33 | 44 | 118.0833 | 99.999 | 28.8333 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16394C | BRISTOL SHIREHAMPTON ROAD NO 100 | 100455 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5539076610 | GB109053027530 | Trym - source to conf R Avon (Brist) | RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 36 | 32 | 23 | 25 | 4.6667 | 83.9753 | 30.6667 | 5 (installed 2018) | Telemetry or data archiving failure / issue | Resolved - May | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2021-05-27 | Sewage fungus and sewage litter present |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16398C | BRISTOL STOKE LANE O/S NO 122 WESTBURY ON TRYM | 013106 | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol North West Boro Const | ST5673577540 | GB109053027530 | Trym - source to conf R Avon (Brist) | RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 70 | 34 | 54 | 78 | 152.2167 | 99.9901 | 59 | 4 (installed 2019) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2023-09-25 | Sewage fungus spotted but no sewage litter |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16424C | BRISTOL DRUID WOOD | 100842 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5526476276 | GB109053027530 | Trym - source to conf R Avon (Brist) | RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 16 | 27 | 26 | 50 | 88.8333 | 99.7116 | 29.75 | 5 (installed 2018) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16613C | POOLE STANLEY GREEN ROAD | 400743 | SO on sewer network |  | Diluted | Rainwater | POOLE | Poole Boro Const | SZ0100192019 | 68 | Not part of a river WB catchment | CREEKMOOR LAKE(VIA SWS) | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA |  |  |  | Commissioned in 2016 - full year data expected | 44 | 32 | 31 | 44 | 140.1333 | 99.9871 | 31.625 | 7 (installed 2016) | [5 empty] | 2023-10-17 | no access |  | N/A |  |  |  |  | Not part of a river WB catchment | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16640C | WOOL STATION ROAD IN GRASS VERGE | 401165 | SO on sewer network |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SY8440086990 | GB108044009692 | Frome Dorset (Lower) d/s Louds Mill Dorchester | TRIB OF RIVER FROME |  |  |  |  | Commissioned in 2019 - full year data expected | 28 | 13 | 12 | 36 | 252.4 | 100 | 24.8333 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009692 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16652C | MERE SHAFTESBURY ROAD | 401431 | SO on sewer network |  | Diluted | Rainwater | SALISBURY | South West Wiltshire Co Const | ST8152031810 | GB108043022450 | Shreen Water (including Ashfield Water) | SHREEN WATER |  |  |  |  | Commissioned in 2019 - full year data expected | 23 | 21 | 19 | 54 | 442.7333 | 99.7546 | 29.25 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022450 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16673C | ILMINSTER BREWERY LANE | 102396 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST3580914482 | GB108052015190 | Isle - Upper to conf Cad Bk | SHUDRICK STREAM |  |  |  |  | Commissioned in 2018 - full year data expected | 41 | 57 | 30 | 32 | 55 | 99.9959 | 42.6667 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2019-08-05 | Sewage fungus and sewage litter present | 2018-04-20 | Lab assessment - No impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015190 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16730C | TRULL EASTBROOK ROAD | 100522/CS/01 | SO on sewer network |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST2178922073 | GB108052015410 | Sherford Stream | SHERFORD STREAM |  |  |  |  | Commissioned in 2018 - full year data expected | 17 | 14 | 9 | 15 | 54.1667 | 99.6648 | 11 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015410 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16768C | MIDSOMER NORTON BERKELEY AVENUE SO | 013129 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6642054720 | GB109053022250 | Wellow Bk - source to conf Snails Bk | WELLOW BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 46 | 28 | 29 | 53 | 141.5 | 99.8626 | 39.2 | 5 (installed 2018) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2022-09-26 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022250 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16774C | MIDSOMER NORTON STORM RETENTION TANK (OLD STW) | 100080 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6779054830 | GB109053022250 | Wellow Bk - source to conf Snails Bk | WELLOW BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 40 | 25 | 26 | 49 | 184.9167 | 99.9857 | 37.4286 | 6 (installed 2017) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2022-09-26 | No sewage litter or sewage fungus |  | N/A | 2023-08-14 | Severe (because of FIS) |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022250 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16779C | STON EASTON HOME FARM SO | 010772 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Wells Co Const | ST6219554110 | GB109053022250 | Wellow Bk - source to conf Snails Bk | TRIB OF WELLOW BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 51 | 33 | 15 | 31 | 19.7333 | 75.4673 | 33 | 5 (installed 2018) | Comms failure / issue | Resolved - Mar |  |  |  | 2022-09-27 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022250 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16790C | MONKTON COMBE MILL LANE | 021680 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST7725661731 | GB109053022271 | Wellow Bk - Snails Bk to Bristol Avon | MIDFORD BROOK (VIA SWS) |  |  |  |  | Commissioned in 2018 - full year data expected | 67 | 47 | 37 | 60 | 77.8333 | 99.9718 | 40.125 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2023-10-09 | No sewage litter or sewage fungus | 2023-10-09 | TBC | 2022-03-01 | Water Quality Modelling shows that the WFD Status Class at the 99%ile level for BOD and Ammonia is High ‘with’ or ‘without’ all Bath FSOs |  | RICT analysis also complete (Very low) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022271 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16793C | FORDINGTON HIGH STREET NO 16 | 400683 | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | SY6963090750 | GB108044009691 | Frome Dorset (Lower) u/s Louds Mill Dorchester | DORCHESTER MILL STREAM |  |  |  |  | Commissioned in 2018 - full year data expected | 17 | 20 | 27 | 65 | 624.5 | 99.9708 | 26.4286 | 5 (installed 2018) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009691 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16795C | DORCHESTER KINGS ROAD NO 35 | 400689 | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | SY7012290514 | GB108044009691 | Frome Dorset (Lower) u/s Louds Mill Dorchester | MILL STREAM VIA SWS |  |  |  |  | Commissioned in 2017 - full year data expected | 29 | 20 | 24 | 45 | 91.4167 | 99.9683 | 25.8571 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009691 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16816C | EVERSHOT COMMON | 042430 | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | ST5762704625 | GB108044009620 | Frome Dorset (Headwaters) | RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 83 | 68 | 63 | 85 | 193.7667 | 99.9433 | 63 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2020-04-03 | Sewage litter present, no sewage fungus | 2020-04-03 | Lab assessment - Impact |  |  |  | RICT analysis complete (Severe) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009620 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16831C | PORTISHEAD HILLSIDE ROAD REDCLIFF BAY | 100563/CS/01 | SO on sewer network |  | Diluted | Rainwater | NORTH SOMERSET | North Somerset Co Const | ST4390375892 | GB530905415405 | BRISTOL AVON | RIVER SEVERN (ESTUARINE) |  |  |  |  | Commissioned in 2018 - full year data expected | 68 | 51 | 37 | 60 | 102.6667 | 98.7922 | 49 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2021-05-26 | No sewage litter or sewage fungus |  | TRAC site - N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16848C | WEYMOUTH CHICKERELL ROAD | 400893 | SO on sewer network |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6758078730 | GB510804415700 | WEY | WEYMOUTH HARBOUR | PORTLAND NORTH EASTERN BREAKWATER |  |  |  | Commissioned in 2019 - full year data expected | 29 | 22 | 27 | 41 | 14.6 | 99.9745 | 22 | 4 (installed 2019) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2021-03-16 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB510804415700 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16855C | WEYMOUTH MELCOMBE AVENUE | 401191 | SO on sewer network |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6859780667 | 427 | Not part of a river WB catchment | TRIB OF WEYMOUTH BAY (VIA SWS) |  | WEYMOUTH LODMOOR | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=lodmoor&site=ukk2206-20600 |  | Commissioned in 2018 - full year data expected | 9 | 6 | 13 | 14 | 6.5667 | 95.0879 | 10.875 | 5 (installed 2018) | [5 empty] | 2023-10-04 | No sewage litter but sewage fungus spotted |  | N/A |  |  |  |  | Not part of a river WB catchment | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16857C | WEYMOUTH RODWELL AVENUE | 400894 | SO on sewer network |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6806078620 | GB510804415700 | WEY | WEYMOUTH HARBOUR VIA SWS (E) |  |  |  |  | Commissioned in 2019 - full year data expected | 49 | 39 | 40 | 55 | 45.8333 | 99.9449 | 52 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2020-11-10 | No sewage litter or sewage fungus |  | N/A |  |  |  | High tide - unable to see outfall | https://environment.data.gov.uk/catchment-planning/WaterBody/GB510804415700 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16861C | WEYMOUTH SPRING LANE | 400896 | SO on sewer network |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6805978622 | GB510804415700 | WEY | WEYMOUTH HARBOUR VIA SWS (E) |  |  |  |  | Commissioned in 2019 - full year data expected | 1 | 0 | 0 | 0 | 0 | 99.9997 | 0.14286 | 4 (installed 2019) | [5 empty] | 2023-10-05 | Sea outfall - fungus spotted at the outfall |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB510804415700 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16863C | WEYMOUTH WARDCLIFFE ROAD | 400898 | SO on sewer network |  | Diluted | Groundwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6758078730 | GB510804415700 | WEY | WEYMOUTH HARBOUR(E) |  |  |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 3 (installed 2020) | [5 empty] | 2023-10-05 | Sea outfall - N/A |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB510804415700 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16888C | BICKNOLLER BICKNOLLER SO | 102303 | SO on sewer network |  | Diluted | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | ST1049939001 | GB108051020250 | Doniford Stream | TRIB OF DONIFORD STREAM (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 31 | 21 | 27 | 48 | 102.2333 | 99.8676 | 30 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108051020250 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17028B | GODMANSTONE | 401521 | Inlet SO at WwTW |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | SY6659096430 | GB108044009710 | Cerne | RIVER CERNE |  |  |  |  | Oct 2023 |  |  |  | 23 | 365.7833 | 91.204 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009710 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17030C | WEYMOUTH ROMAN ROAD NEW | 401188 | SO on sewer network |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6721080970 | GB108044010210 | Wey | RADIPOLE LAKE (S) |  |  |  |  | Commissioned in 2020 - full year data expected |  | 40 | 37 | 48 | 37.8333 | 99.9954 | 41.6667 | 3 (installed 2020) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2023-10-04 | no access |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010210 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17501C | BRISTOL CRANBROOK ROAD O/S NO 2 | 100872 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5611874456 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2018 - full year data expected | 46 | 54 | 45 | 58 | 54.5 | 91.4867 | 50.75 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2023-09-28 | too deep |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
18015C | BOURNEMOUTH COOPER DEAN DETENTION TANK | 041221 | SO on sewer network |  | Diluted and partially treated | Rainwater | BOURNEMOUTH | Bournemouth East Boro Const | SZ1313593804 | GB108043011040 | Stour (Lower) | RIVER STOUR VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 19 | 11 | 12 | 28 | 84.0911 | 99.8502 | 15.8333 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011040 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19030C | BRISTOL MERLIN CLOSE VORTEX | 013101 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5673677540 | GB109053027530 | Trym - source to conf R Avon (Brist) | RIVER TRYM |  |  |  |  | Commissioned in 2019 - full year data expected | 31 | 31 | 21 | 35 | 50.0167 | 99.993 | 29.5 | 4 (installed 2019) | [5 empty] | 2023-09-25 | No sewage litter but sewage fungus spotted |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19052C | BOX BOX RECREATION GROUND (ADJ TO) | 101679 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST8232768729 | GB109053027380 | By Bk - conf Doncombe Bk to conf R Avon (Brist) | BY BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 51 | 55 | 35 | 55 | 39.0667 | 99.6823 | 45.8333 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2021-03-29 | No sewage litter or sewage fungus |  | N/A | 2022-03-01 | Water Quality Modelling shows no impact |  | Multiple overflows so unsuitable for invertebrate assessment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027380 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19293C | BRISTOL GLOUCESTER ROAD/CAMBRIDGE ROAD | 013053 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5611874456 | GB530905415405 | BRISTOL AVON | BRISTOL AVON VIA SWS ESTUARINE |  |  |  |  | Commissioned in 2018 - full year data expected | 23 | 28 | 29 | 43 | 31 | 99.4939 | 30.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19541S | SWANAGE MARINE PARADE TUNNEL | 400785 | Storm tank at WwTW |  | Diluted | Rainwater | PURBECK | South Dorset Co Const | SZ0424378665 | GB620705550000 | Dorset / Hampshire | SWANAGE BAY |  | SWANAGE CENTRAL | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=swanage&site=ukk2204-19800 |  | Commissioned in 2018 - full year data expected | 29 | 19 | 15 | 38 | 166.11 | 100 | 29.875 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620705550000 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19699B | BOVINGTON LYTCHETT LANE | 401064 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SY8424687947 | GB108044009692 | Frome Dorset (Lower) d/s Louds Mill Dorchester | TRIBUTARY OF RIVER FROME |  |  |  |  | Commissioned in 2019 - full year data expected | 15 | 10 | 3 | 11 | 39.8333 | 100 | 9.75 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009692 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19705S | WATCHET STORM TANK | 101940 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | ST0652044550 | GB640807670000 | Bristol Channel Inner South | BRISTOL CHANNEL(C) |  | BLUE ANCHOR WEST | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=blue%20a&site=ukk2305-35200 |  | Commissioned in 2016 - full year data expected | 66 | 3 | 13 | 73 | 1210.5 | 100 | 35 | 7 (installed 2016) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB640807670000 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19723C | WOOKEY HOLE GLEN COTTAGE GLENCOTT LANE | 102592 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Wells Co Const | ST5313846920 | GB109052021520 | Axe - source to Cocklake | RIVER AXE |  |  |  |  | Commissioned in 2018 - full year data expected | 36 | 23 | 21 | 56 | 88.7333 | 99.9201 | 28 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021520 | No |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19985C | MIDSOMER NORTON NORTHMEAD ROAD/ HAYES PARK ROAD | 101866 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6581054730 | GB109053022250 | Wellow Bk - source to conf Snails Bk | WELLOW BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 21 | 13 | 11 | 19 | 46.8667 | 99.8733 | 15.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022250 | Yes |  |  | 2030 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13017S | BECKINGTON STORM TANK | 011987 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | MENDIP | Somerton and Frome Co Const | ST7962051970 | GB109053021840 | Somerset Frome conf with Mells to conf B. Avo | RIVER FROME |  |  |  |  | Commissioned in 2019 - full year data expected | 61 | 15 | 20 | 31 | 458.9333 | 100 | 29.6 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021840 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13056S | CHARMOUTH STORM TANKS STORM TANK | 401625 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | SY3717093740 | GB620806560000 | Lyme Bay East | RIVER CHAR |  | CHARMOUTH WEST | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=charm&site=ukk2205-21300 |  | Commissioned in 2016 - full year data expected | 4 | 2 | 1 | 7 | 56.639 | 100 | 3.5 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620806560000 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13064S | CHIPPENHAM BLACKWELL HAMS STORM TANK | 101637 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | NORTH WILTSHIRE | Chippenham Co Const | ST9176371284 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 60 | 31 | 46 | 84 | 1219.4333 | 94.8014 | 55.4 | 5 (installed 2018) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2022-05-09 | No sewage litter or sewage fungus | 2022-05-09 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13069S | COLEFORD STORM TANK | 010265 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | MENDIP | Somerton and Frome Co Const | ST6917148925 | GB109053022020 | Mells source to conf with Somerset Frome | MELLS RIVER |  |  |  |  | Commissioned in 2017 - full year data expected | 112 | 76 | 85 | 119 | 1654.5 | 100 | 98.5 | 6 (installed 2017) |  |  | Performance - Infiltration | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2020-03-19 | Sewage litter present, no sewage fungus | 2021-03-19 | Field based assessment - No impact |  |  |  | RICT analysis complete (Impact high) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022020 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13096S | DORCHESTER LOUDS MILL ST GEORGES ROAD STORM TANKS STORM TANK | 401050 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | SY7116090340 | GB108044009692 | Frome Dorset (Lower) d/s Louds Mill Dorchester | RIVER FROME(S) |  |  |  |  | Commissioned in 2020 - full year data expected |  | 10 | 48 | 109 | 1474.2833 | 100 | 55.6667 | 3 (installed 2020) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009692 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13134S | GLASTONBURY THE BECKERY STORM TANK | 101431 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | MENDIP | Wells Co Const | ST4819438006 | GB108052021190 | Brue - Clyce Hole to conf North Drain | GLAST MILL STREAM & RIVER BRUE |  |  |  |  | Commissioned in 2016 - full year data expected | 71 | 63 | 48 | 94 | 1267 | 100 | 55.875 | 7 (installed 2016) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2020-11-06 | No sewage litter or sewage fungus | [6 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021190 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13136S | GREAT BADMINTON STORM TANK | 010039 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST8169783054 | GB109053027665 | Luckington Bk | LUCKINGTON BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 208 | 116 | 111 | 167 | 3654.9 | 99.8135 | 149.5 | 6 (installed 2017) |  |  | Performance - Infiltration | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2020-03-12 | Sewage fungus and sewage litter present | [5 empty] | RICT unsuitable | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027665 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13145C | HATCH BEAUCHAMP PALMER GREEN INLET | 070053 | Inlet SO at WwTW |  | Diluted | A combination of rainwater and groundwater | TAUNTON DEANE | Taunton Deane Co Const | ST3070219656 | GB108052015241 | Fivehead River | FIVEHEAD RIVER |  |  |  |  | Commissioned in 2018 - full year data expected | 134 | 139 | 131 | 199 | 964.45 | 99.9338 | 147.8 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2021-09-24 | Sewage fungus present no sewage litter | 2021-09-24 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015241 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13149C | HINDON INLET | 402489 | Inlet SO at WwTW - with treatment | Reed bed | Fully treated | Rainwater | SALISBURY | South West Wiltshire Co Const | ST9165032750 | GB108043022500 | Fonthill Stream | GROUNDWATER VIA INFILT SYSTEM |  |  |  |  | Commissioned in 2019 - full year data expected | 40 | 77 | 46 | 113 | 1017.7958 | 87.55 | 55.2 | 4 (installed 2019) | Sensor failure / issue | Resolved - Sep | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2023-09-26 | No sewage litter or sewage fungus |  | N/A |  |  |  | Has wetland treatment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022500 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13157S | HULLAVINGTON STORM TANK | 101441 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST8962382856 | GB109053027730 | Gauze Bk - source to conf R Avon (Brist) | GAUZE BROOK (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 151 | 85 | 77 | 138 | 2604.3667 | 99.8946 | 117 | 5 (installed 2018) |  |  | Performance - GW inundation | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2020-11-17 | No sewage litter or sewage fungus | [6 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027730 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13160S | ILCHESTER PILL BRIDGE LANE STORM TANK | 101879 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | SOUTH SOMERSET | Yeovil Co Const | ST5156822864 | GB108052015682 | Yeo Ds Over Compton | RIVER YEO |  |  |  |  | Commissioned in 2018 - full year data expected | 15 | 16 | 27 | 48 | 709.3667 | 98.9315 | 26 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015682 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13165S | KEYNSHAM STORM TANK | 102362 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6610068910 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 85 | 68 | 54 | 84 | 963.3667 | 99.8916 | 74.2 | 5 (installed 2018) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2021-05-27 | Sewage litter present, no sewage fungus | 2021-05-27 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13195C | MAPPOWDER INLET | 040055 | Inlet SO at WwTW |  | Diluted | Groundwater | NORTH DORSET | North Dorset Co Const | ST7381806650 | GB108043015900 | Wonston Brook | TRIB OF THE RIVER LYDDEN |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 61 | 127 | 2668.4833 | 99.9994 | 94 | 2 (installed 2021) |  |  | Performance - Infiltration | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015900 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13201S | MARTOCK HURST BOW STORM TANK | 100288 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST4439019940 | GB108052015350 | Wellhams Brook | PARRETT AND HINTON MEADS BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 63 | 56 | 51 | 110 | 1450.4 | 99.6313 | 57.1667 | 6 (installed 2017) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2021-05-10 | Sewage litter present, no sewage fungus | 2021-05-10 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015350 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13204B | MELKSHAM INLET | 101886 | Inlet SO at WwTW |  | Diluted | Rainwater | WEST WILTSHIRE | Chippenham Co Const | ST9008063900 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | RIVER AVON |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 37 | 70 | 935.0667 | 99.7295 | 53.5 | 2 (installed 2021) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13221S | NORTH CADBURY RIDGEWAY LANE STORM TANK | 102410 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST6287027309 | GB108052015690 | Cam - Upper | RIVER CAM |  |  |  |  | Commissioned in 2019 - full year data expected | 84 | 63 | 48 | 106 | 1666.95 | 100 | 67.4 | 4 (installed 2019) |  |  | Performance - Infiltration | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2020-11-24 | No sewage litter or sewage fungus | [6 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015690 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13242S | POOLE CABOT LANE STORM TANK | 401354 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | POOLE | Poole Boro Const | SZ0071093560 | GB520804415800 | POOLE HARBOUR | TRIBUTARY OF HOLES BAY(E) | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA | POOLE HARBOUR HAMWORTH PARK /POOLE HARBOUR ROCKLEY SANDS / POOLE HARBOUR LAKE | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=rockl&site=ukk2102-19450 | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=harbour%20lake&site=ukk2102-19400 | Commissioned in 2016 - full year data expected | 17 | 10 | 16 | 20 | 193 | 99.9914 | 15.125 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB520804415800 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13268C | SHERBORNE WEST MILL LANE INLET | 070099 | Inlet SO at WwTW |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | ST6301515348 | GB108052015630 | Yeo | RIVER YEO |  |  |  |  | Commissioned in 2018 - full year data expected | 26 | 17 | 26 | 38 | 546.5333 | 99.2439 | 26.6667 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015630 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13290S | STOKE ST GREGORY STORM TANK | 070379 | Inlet SO at WwTW |  | Diluted | A combination of rainwater and groundwater | TAUNTON DEANE | Taunton Deane Co Const | ST3354027530 | GB540805210900 | Parrett | TIDAL RIVER TONE(E) |  |  |  |  | Commissioned in 2019 - full year data expected | 41 | 22 | 3 | 7 | 114.0833 | 99.8896 | 20 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB540805210900 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13298C | SUTTON BENGER INLET | 010083 | Inlet SO at WwTW |  | Diluted | Groundwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9579078610 | GB109053027650 | Avon (Brist) conf Tetbury Avon to conf R Marden | BRISTOL AVON(S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 46 | 92 | 1683.3893 | 99.9975 | 69 | 1 (installed 2022) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027650 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13308S | THINGLEY COPPERSHELL LANE STORM TANK | 102328 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | NORTH WILTSHIRE | Chippenham Co Const | ST9190067590 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | BYDE MILL BROOK/RIVER AVON |  |  |  |  | Commissioned in 2019 - full year data expected | 39 | 40 | 44 | 65 | 977 | 99.9897 | 44.6 | 4 (installed 2019) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2023-11-06 | No sewage litter or sewage fungus | 2023-11-06 | TBC |  |  |  | RICT analysis complete (LOW) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13309Z | THORNBURY STORM TANK | 102442 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6280092340 | GB109054026670 | Oldbury Naite Rhine | SEVERN ESTUARY(E) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 15 | 67 | 1310.4667 | 99.6412 | 41 | 1 (installed 2022) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026670 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13342B | WEYMOUTH INLET | 400622 | Inlet SO at WwTW |  | Diluted and partially treated | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6613074360 | GB620806560000 | Lyme Bay East | (C) ENGLISH CHANNEL |  |  |  |  | Commissioned in 2019 - full year data expected | 78 | 66 | 59 | 90 | 424.0589 | 95.3744 | 77.2 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2022-09-28 | No sewage litter or sewage fungus | 2022-09-28 | TRAC site - N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620806560000 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13358S | WOOKEY STORM TANK | 070130 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | MENDIP | Wells Co Const | ST5075545603 | GB109052021520 | Axe - source to Cocklake | RIVER AXE |  |  |  |  | Commissioned in 2019 - full year data expected | 134 | 66 | 62 | 197 | 3509.4 | 99.876 | 118.8 | 4 (installed 2019) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2021-03-19 | No sewage litter or sewage fungus | 2021-03-19 | Incomplete |  |  |  | No upstream inverts samples | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021520 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13362S | WORTH MATRAVERS STORM TANK | 400606 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SY9736276843 | 250 | Not part of a river WB catchment | STREAM AT WINSPIT BOTTTOM |  |  |  |  | Commissioned in 2017 - full year data expected | 44 | 19 | 21 | 36 | 116.9919 | 99.857 | 49.1667 | 6 (installed 2017) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2023-05-26 | No sewage litter or sewage fungus | 2023-05-26 | TBC |  |  |  |  | Not part of a river WB catchment | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13364S | WRINGTON | 102486 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | NORTH SOMERSET | North Somerset Co Const | ST4640762639 | GB109052021640 | Yeo - source to conf Congresbury Yeo | TRIB OF CONGRESBURY YEO(S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 8 | 67 | 1165.1833 | 99.9775 | 37.5 | 1 (installed 2022) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2023-10-13 | No sewage litter or sewage fungus | 2023-10-13 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021640 | Yes |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14017B | BRISTOL BLACK ROCKS PORTWAY | 101844 | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol North West Boro Const | ST5612174457 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2019 - full year data expected | 43 | 50 | 39 | 60 | 631.7492 | 93.5835 | 37.8571 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2023-09-28 | too deep to see |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14050B | COLLINGBOURNE DUCIS | 401764 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | KENNET | Devizes Co Const | SU2434853472 | GB108043022390 | Bourne (Hampshire Avon) | RIVER BOURNE |  |  |  |  | Commissioned in 2019 - full year data expected | 115 | 59 | 6 | 101 | 316.6542 | 100 | 60.4 | 4 (installed 2019) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2022-11-17 | No sewage litter or sewage fungus | 2022-11-17 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022390 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14096B | COXLEY MILL LANE | 102834 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Wells Co Const | ST5302343805 | GB108052021221 | Sheppey | RIVER SHEPPEY |  |  |  |  | Commissioned in 2019 - full year data expected | 43 | 53 | 54 | 75 | 352.6399 | 100 | 46.5 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" |  |  |  |  | 2022-01-14 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021221 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14116B | GURNEY SLADE | 101865 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | MENDIP | Wells Co Const | ST6334049540 | GB109053022020 | Mells source to conf with Somerset Frome | MELLS STREAM(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 50 | 30 | 5 | 39 | 463.95 | 99.9751 | 33.8 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022020 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14139B | CHRISTIAN MALFORD SWALLETTS GATE | NPSWQD004959 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9864480753 | GB109053027710 | The Bourne - source to conf R Avon (Brist) | TRIBUTARY OF THE BOURNE |  |  |  |  | Commissioned in 2019 - full year data expected | 47 | 6 | 27 | 34 | 116.6451 | 99.994 | 28.5 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027710 | Yes |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14151B | DAUNTSEY THE GREEN | 102280 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9955081930 | GB109053027710 | The Bourne - source to conf R Avon (Brist) | DAUNTSEY BROOK(S) |  |  |  |  | Commissioned in 2020 - full year data expected | 1 | 11 | 12 | 42 | 325.1648 | 100 | 16.5 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027710 | Yes |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14174B | BOX MILL LANE | 011833 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST8246568899 | GB109053027380 | By Bk - conf Doncombe Bk to conf R Avon (Brist) | BY BROOK |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 37 | 56 | 273.5333 | 100 | 46.5 | 2 (installed 2021) | [9 empty] | 2023-01-09 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027380 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14240B | BOVINGTON MORRIS ROAD | 401421 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SY8406988509 | GB108044009692 | Frome Dorset (Lower) d/s Louds Mill Dorchester | TRIBUTARY OF THE RIVER FROME |  |  |  |  | Commissioned in 2020 - full year data expected |  | 6 | 30 | 46 | 296.2833 | 99.756 | 27.3333 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009692 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14276B | CORFE CASTLE STUDLAND ROAD | 401429 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SY9605782638 | GB108044010020 | Corfe River | CORFE RIVER |  |  |  |  | Commissioned in 2018 - full year data expected | 28 | 18 | 8 | 20 | 25.3497 | 99.9741 | 24.4 | 5 (installed 2018) | [5 empty] | 2021-11-16 | No sewage litter or sewage fungus | 2021-11-16 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010020 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14304B | ALLINGTON OLD INN | 401580 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | SALISBURY | Salisbury Co Const | SU2053339325 | GB108043022390 | Bourne (Hampshire Avon) | RIVER BOURNE |  |  |  |  | Commissioned in 2019 - full year data expected | 93 | 11 | 0 | 49 | 1004.75 | 98.0642 | 30.6 | 4 (installed 2019) | [5 empty] | 2022-11-17 | No sewage litter or sewage fungus | 2022-11-17 | TBC | 2022-12-30 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022390 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14346B | HINDON THE DENE | 042095 | Storm discharge at pumping station |  | Diluted | Rainwater | SALISBURY | South West Wiltshire Co Const | ST9172432927 | GB108043022500 | Fonthill Stream | TRIBUTARY OF THE RIVER NADDER |  |  |  |  | Commissioned in 2019 - full year data expected | 75 | 23 | 9 | 14 | 73.5 | 96.0821 | 30.8 | 4 (installed 2019) | [5 empty] | 2022-11-16 | No sewage litter or sewage fungus | 2022-11-16 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022500 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14371B | CHEDDAR FROGLANDS | 101665 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Wells Co Const | ST4604052990 | GB109052021540 | Cheddar Yeo - source to conf Stubbingham Rhyne | RIVER YEO (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 81 | 32 | 34 | 83 | 174.3151 | 100 | 57.5 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2023-11-04 | No sewage litter or sewage fungus | 2023-11-04 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021540 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14389C | TAUNTON PRIORY STORM TANKS CSO | 102258 | SO on sewer network |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST2360025410 | GB108052015482 | Tone Ds Taunton | RIVER TONE(S) |  |  |  |  | Commissioned in 2019 - full year data expected | 39 | 23 | 15 | 27 | 208.1975 | 100 | 24.8 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015482 | Yes |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14389S | TAUNTON PRIORY STORM TANKS STORM TANKS | 102258 | Other storm discharge asset type |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST2360025410 | GB108052015482 | Tone Ds Taunton | RIVER TONE(S) |  |  |  |  | Commissioned in 2019 - full year data expected | 68 | 26 | 38 | 75 | 756.6633 | 100 | 50 | 4 (installed 2019) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015482 | Yes |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14397B | BEER HACKETT | NPSWQD008609 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | WEST DORSET | West Dorset Co Const | ST5985811677 | GB108052015570 | Wriggle | WRIGGLE RIVER |  |  |  |  | Commissioned in 2018 - full year data expected | 65 | 19 | 19 | 58 | 598.5 | 99.75 | 53.3333 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2020-04-03 | Sewage litter present, no sewage fungus | 2020-04-03 | Lab assessment - Impact |  |  |  | RICT analysis complete (Extremely severe) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015570 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14432B | COMPTON DANDO TURNBRIDGE | 103604 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6474064690 | GB109053021950 | Chew - conf Winford Bk to conf R Avon (Brist) | RIVER CHEW(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 41 | 47 | 43 | 74 | 1103.65 | 99.9618 | 51.25 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" |  |  |  |  | 2021-12-01 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021950 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14495C | CLEVEDON MAIN | 102134 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH SOMERSET | North Somerset Co Const | ST3923070290 | GB530905415405 | BRISTOL AVON | BRISTOL CHANNEL |  | CLEVEDON BEACH | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=cleved&site=ukk1202-36000 |  | Commissioned in 2016 - full year data expected | 14 | 10 | 3 | 16 | 52.5103 | 100 | 6.375 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14501C | BRISTOL WHITBY ROAD ST ANNES | 021440 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6152072542 | 157 | Not part of a river WB catchment | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 10 | 20 | 10 | 15 | 14.6333 | 99.7203 | 11.1667 | 5 (installed 2018) | [13 empty] | Not part of a river WB catchment | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15013B | SOUTHBOURNE HENGISTBURY HEAD | 400550 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BOURNEMOUTH | Bournemouth East Boro Const | SZ1589090520 | GB620705550000 | Dorset / Hampshire | POOLE BAY (C) |  | BOURNEMOUTH HENGISTBURY WEST | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=bournem&site=ukk2101-19000 |  | Commissioned in 2016 - full year data expected | 25 | 20 | 16 | 29 | 88.5 | 99.9997 | 19.75 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620705550000 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15019B | BOURNEMOUTH NO 1 | 400758 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BOURNEMOUTH | Bournemouth West Boro Const | SZ0920090210 | GB620705550000 | Dorset / Hampshire | POOLE BAY (C) |  | BOURNEMOUTH PIER | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=bournem&site=ukk2101-19100 |  | Commissioned in 2016 - full year data expected | 7 | 7 | 10 | 10 | 23.6406 | 100 | 8.125 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620705550000 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15072B | FERNDOWN AMEYSFORD ROAD | 400646 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | EAST DORSET | Christchurch Co Const | SU0701002124 | GB108043011080 | Uddens Water | TRIBUTARY OF UDDENS WATER |  |  |  |  | Commissioned in 2018 - full year data expected | 14 | 13 | 13 | 21 | 73.9167 | 99.9563 | 13.6 | 5 (installed 2018) | [7 empty] | 2020-05-01 | Lab assessment - Impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011080 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15252B | POOLE EGMONT ROAD | 402037 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | POOLE | Poole Boro Const | SY9764791734 | GB520804415800 | POOLE HARBOUR | LYTCHETT BAY (SWS) ESTUARINE | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA | POOLE HARBOUR ROCKLEY SANDS | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=rockl&site=ukk2102-19450 |  | Commissioned in 2016 - full year data expected | 0 | 10 | 2 | 8 | 44.25 | 95.5065 | 3.75 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB520804415800 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15573B | BLEADON PURN | 101663 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | NORTH SOMERSET | Weston-Super-Mare Co Const | ST3372056950 | GB109052021570 | Axe - Cocklake to Brean Cross Sluice | NEW RHYNE(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 52 | 25 | 3 | 46 | 720 | 99.8945 | 31.5 | 5 (installed 2018) | [9 empty] | 2022-06-21 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021570 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15507B | BRIDPORT WEST BAY SLUICES | 402047 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | SY4621090490 | GB620806560000 | Lyme Bay East | BRIDPORT HARBOUR(WEST BAY)(C) |  | WEST BAY (WEST) | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=west%20bay&site=ukk2205-21000 |  | Commissioned in 2016 - full year data expected | 14 | 13 | 23 | 32 | 318.35 | 100 | 17.875 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620806560000 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15519B | WATCHET MARKET STREET (TUNNEL) | 101270 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | ST0700043470 | 421 | Not part of a river WB catchment | (S) WASHFORD RIVER |  | BLUE ANCHOR WEST | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=blue%20a&site=ukk2305-35200 |  | Commissioned in 2016 - full year data expected | 33 | 15 | 13 | 38 | 209.3667 | 99.999 | 14.75 | 7 (installed 2016) | [13 empty] | Not part of a river WB catchment | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15541B | KEYNSHAM THE HAMS | 013093 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6493569732 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2019 - full year data expected | 53 | 46 | 55 | 95 | 90.5861 | 100 | 62.25 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" |  |  |  |  | 2022-01-11 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15606B | CLEVEDON THE BEACH | 100767 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH SOMERSET | North Somerset Co Const | ST4021071730 | GB530905415405 | BRISTOL AVON | BRISTOL CHANNEL (E) |  | CLEVEDON BEACH | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=cleved&site=ukk1202-36000 |  | Commissioned in 2016 - full year data expected | 6 | 7 | 1 | 11 | 9.8 | 94.1054 | 8.625 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15645B | PILL AVON ROAD | 011673 | Storm discharge at pumping station |  | Diluted | Rainwater | NORTH SOMERSET | North Somerset Co Const | ST5228676403 | GB530905415405 | BRISTOL AVON | RIVER AVON (ESTUARINE) |  |  |  |  | Commissioned in 2019 - full year data expected | 66 | 46 | 36 | 54 | 144.05 | 99.61 | 44 | 4 (installed 2019) |  |  | Data collection - Tidal / river inundation | Resolved - Nov | N/A - Operational solution applied | 2023-09-25 | No sewage litter or sewage fungus | 2023-05-22 | N/A - TRAC site |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15680B | PORTISHEAD BLACK NORE (NAUTICAL SCHOOL) | 071587 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH SOMERSET | North Somerset Co Const | ST4445276495 | GB530905415405 | BRISTOL AVON | SEVERN ESTUARY |  |  |  |  | Commissioned in 2019 - full year data expected | 53 | 15 | 28 | 51 | 156.8333 | 99.941 | 43 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2022-10-10 | No sewage litter or sewage fungus |  | TRAC site - N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15726B | PORTISHEAD LAKE GROUNDS | 101909 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | NORTH SOMERSET | North Somerset Co Const | ST4611077040 | GB530905415405 | BRISTOL AVON | ESTUARY (E) |  |  |  |  | Commissioned in 2018 - full year data expected | 22 | 7 | 9 | 10 | 89.9 | 99.7546 | 12 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16013C | BATH HAZEL GROVE R/O NO 24 TO 39 | 102603 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7390765092 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 22 | 33 | 7 | 11 | 1.5 | 99.6024 | 18.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16014C | BATH BECKHAMPTON ROAD O/S NO 50 | 102606 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7391065090 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 46 | 22 | 8 | 40 | 202.4333 | 98.7751 | 30.2 | 5 (installed 2018) | [5 empty] | 2022-03-15 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16016C | BATH MOORLAND ROAD NEAR NO 49 | 102781 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7390765093 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 51 | 41 | 38 | 54 | 46.7333 | 99.9722 | 45.8 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2021-03-29 | Sewage litter present, no sewage fungus | [6 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16018C | BATH HISCOCKS DRIVE ADJ TO RAILWAY BRIDGE | 010941 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7390865092 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 40 | 35 | 28 | 33 | 18.4667 | 99.6465 | 29 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16019C | BATH DURLEY PARK / OLDFIELD LANE JUNCTION | 010940 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7390865093 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 48 | 37 | 36 | 54 | 31.5333 | 99.1884 | 43.75 | 5 (installed 2018) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16040C | BATH NORFOLK BUILDINGS | 102273 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7434864830 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2019 - full year data expected | 32 | 26 | 28 | 33 | 149.3667 | 99.9979 | 25.5714 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16057C | BATH TECHNOLOGY HOUSE | 102276 | SO on sewer network |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7293364761 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2017 - full year data expected | 19 | 16 | 18 | 25 | 266.25 | 99.999 | 17.1429 | 6 (installed 2017) | [9 empty] | 2021-10-25 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16058C | BATH FIELDINGS ROAD | 010914 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7307564793 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 26 | 22 | 20 | 16 | 4.3667 | 94.4387 | 21 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16059C | BATH STATION ROAD S/O 44 LOCKSBROOK ROAD | EPRAP3920XP | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7303764818 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 26 | 11 | 16 | 23 | 135.2 | 99.9996 | 16.8333 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16090C | BATH SPRING GARDENS ROAD U/S K&A CANAL SYPHON | 010883 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7538664312 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 21 | 16 | 20 | 26 | 255.7333 | 99.6107 | 17.6667 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16095C | BATH PRIOR PARK ROAD | NPSWQD002498 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7539064300 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2017 - full year data expected | 67 | 49 | 38 | 58 | 44.4667 | 99.8539 | 53.5 | 6 (installed 2017) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2020-11-30 | Sewage litter present, no sewage fungus |  | N/A | 2022-03-01 | Water Quality Modelling shows that the WFD Status Class at the 99%ile level for BOD and Ammonia is High ‘with’ or ‘without’ all Bath FSOs |  | Multiple overflows so unsuitable for invertebrate assessment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16096C | BATH LYNCOMBE VALE O/S NO 1 | NPSWQD002499 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7536064290 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 23 | 16 | 10 | 12 | 1.5333 | 99.7553 | 12.1667 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16098C | BATH WIDCOMBE BAPTIST CHURCH AT REAR CLAVERTON | 101190 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7536064290 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 31 | 36 | 25 | 32 | 26.0333 | 97.2466 | 31.8 | 5 (installed 2018) | [5 empty] | 2021-03-29 | Sewage litter present, no sewage fungus |  | N/A | 2022-03-01 | Water Quality Modelling shows that the WFD Status Class at the 99%ile level for BOD and Ammonia is High ‘with’ or ‘without’ all Bath FSOs |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16110C | BATH BLOOMFIELD ROAD NO 33 JUNCTION WITH HENSLEY ROAD | 102778 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7390865093 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 49 | 47 | 33 | 46 | 29.5 | 92.4197 | 43.75 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16112C | BATH WELLSWAY / BLOOMFIELD ROAD JUNCTION BEAR FLAT | 101923 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7390865093 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 96.7131 | 0 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16115C | BATH WESTMORELAND ROAD / CHELTENHAM STREET JUNCTION | 102779 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7443564584 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 13 | 8 | 8 | 12 | 8.4667 | 99.9235 | 10.4 | 5 (installed 2018) | [5 empty] | 2018-02-05 | [6 empty] | Unable to tell if litter was sewage litter or plastic bags | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16116C | BATH LOWER BRISTOL ROAD WEST OF OAK STREET | 010891 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7469064430 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 32 | 51 | 225.2667 | 99.8128 | 41.5 | 2 (installed 2021) | [5 empty] | 2023-09-26 | No sewage litter spotted, too dep to assess fungus presence |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16117C | BATH CHURCHILL BRIDGE ISLAND OPP WELLS ROAD | 101228 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7496764338 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 32 | 35 | 28 | 36 | 19.1 | 99.9532 | 31 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16119C | BATH RUSH HILL OPP CULVERHAY SCHOOL | 101925 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7343064930 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 30 | 25 | 20 | 24 | 4.1 | 99.7538 | 26.6 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16123C | BATH ENGLISHCOMBE LANE / SOUTHDOWN ROAD JUNCTION | 101929 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7343064930 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 38 | 50 | 46 | 59 | 39.9 | 94.3417 | 43.2 | 5 (installed 2018) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16131C | BOURNEMOUTH TUCKTON ROAD O/S 156 | 401566 | SO on sewer network |  | Diluted | Rainwater | BOURNEMOUTH | Bournemouth East Boro Const | SZ1477092290 | GB520804315900 | CHRISTCHURCH HARBOUR | TIDAL RIVER STOUR(E) |  | CHRISTCHURCH AVON BEACH/CHRISTCHURCH FRIAR'S CLIFF | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=avon%20b&site=ukk2201-18800 | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=friar&site=ukk2201-18750 | Commissioned in 2016 - full year data expected | 12 | 13 | 9 | 16 | 10.4518 | 88.0663 | 10.375 | 7 (installed 2016) | Capital / maintenance works affect EDM operation | Resolved - January after reporting year | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB520804315900 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16134C | BRISTOL AVONMOUTH WAY | 102068 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5202277004 | GB530905415405 | BRISTOL AVON | RIVER AVON (E) VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 27 | 23 | 12 | 25 | 60.0333 | 99.6815 | 21.75 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16136C | BRISTOL OLD PARK ROAD O/S NO 45 | 102090 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5202277004 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2018 - full year data expected | 30 | 22 | 16 | 24 | 3.3333 | 74.1781 | 23 | 5 (installed 2018) | Telemetry or data archiving failure / issue | Resolved - Sep | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16137C | BRISTOL PORTWAY UNDER AVON BRIDGE | 101997 | Storm discharge at pumping station |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5202277005 | GB530905415405 | BRISTOL AVON | RIVER AVON |  |  |  |  | Commissioned in 2019 - full year data expected | 55 | 67 | 56 | 71 | 195.75 | 99.9914 | 49.8 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2023-09-25 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16139C | BRISTOL PORTWAY NEAR RAILWAY | 102112 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5255176337 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2016 - full year data expected | 114 | 94 | 77 | 54 | 99.5333 | 50.2451 | 81 | 7 (installed 2016) | Installation set-up/design issue | Resolved - Sep | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2020-11-03 | No sewage litter or sewage fungus |  | TRAC site - N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16142C | BRISTOL SPRINGFIELD AVENUE O/S NO 5 | 102092 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5263276269 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2018 - full year data expected | 37 | 28 | 25 | 35 | 7.7667 | 100 | 31.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16143C | BRISTOL SPRINGFIELD AVENUE O/S NO 7 | 102093 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5263276269 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2018 - full year data expected | 28 | 34 | 15 | 18 | 2.3667 | 94.1553 | 23.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16146C | BRISTOL THIRD WAY | 102070 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5132579837 | GB530905415405 | BRISTOL AVON | RIVER SEVERN ESTUARY VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 25 | 26 | 13 | 25 | 68.6333 | 99.9741 | 22.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16155C | BRISTOL BATH ROAD TRADING ESTATE | 100589/CS/01 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6093071894 | 157 | Not part of a river WB catchment | RIVER AVON (ESTUARINE) |  |  |  |  | Commissioned in 2019 - full year data expected | 11 | 13 | 8 | 10 | 9.4 | 99.6305 | 10.5 | 4 (installed 2019) | [13 empty] | Not part of a river WB catchment | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16193C | BRISTOL COMMERCIAL ROAD / BEDMIN BRIDGE | 102830 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5895072053 | GB530905415405 | BRISTOL AVON | RIVER AVON (ESTUARINE) |  |  |  |  | Commissioned in 2017 - full year data expected | 13 | 14 | 13 | 17 | 68.0833 | 99.9381 | 11.4286 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16195C | BRISTOL FEEDER ROAD / BARTON HILL BRIDGE | 101099 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST6134272479 | 157 | Not part of a river WB catchment | RIVER AVON (ESTUARINE) |  |  |  |  | Commissioned in 2018 - full year data expected | 16 | 13 | 8 | 18 | 64.2 | 99.7173 | 13.75 | 5 (installed 2018) | [13 empty] | Not part of a river WB catchment | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16204C | BRISTOL PORTWAY NEAR PLIMSOLL BRIDGE (PUMPED) | 102901 | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol West Boro Const | ST5664272585 | 157 | Not part of a river WB catchment | RIVER AVON (ESTUARINE) |  |  |  |  | Commissioned in 2017 - full year data expected | 36 | 42 | 38 | 47 | 308 | 99.9121 | 42.5714 | 6 (installed 2017) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2020-04-29 | No sewage litter or sewage fungus | [5 empty] | Too deep for sewage fungus assessment | Not part of a river WB catchment | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16207C | BRISTOL VICTOR STREET | 101098 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5997771997 | 157 | Not part of a river WB catchment | RIVER AVON (ESTUARINE) VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 15 | 14 | 9 | 11 | 14 | 98.5411 | 12.25 | 5 (installed 2018) | [13 empty] | Not part of a river WB catchment | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16209C | BRISTOL WHITEHALL ROAD O/S NO 46 | 103016 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5612074460 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2017 - full year data expected | 20 | 32 | 23 | 38 | 43.0833 | 99.9838 | 19 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16210C | BRISTOL VALLEY ROAD ZIG ZAG PATH BRIDGE | 101075 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5629373768 | 157 | Not part of a river WB catchment | RIVER AVON (ESTUARINE) VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 22 | 29 | 24 | 36 | 19.2 | 99.6046 | 27.75 | 5 (installed 2018) | [13 empty] | Not part of a river WB catchment | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16279C | BRISTOL MYRTLE ST IN CAR PARK | 103306 | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol South Boro Const | ST5807972113 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2019 - full year data expected | 40 | 38 | 23 | 39 | 36.6333 | 99.8409 | 33.6 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16298C | BRISTOL COTHAM BROW O/S NO 137 | 100873 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5616074420 | GB530905415405 | BRISTOL AVON | RIVER AVON(E) |  |  |  |  | Commissioned in 2019 - full year data expected | 52 | 48 | 42 | 61 | 32.6667 | 99.9682 | 50.4 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2021-05-27 | Sewage litter present, no sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16299C | BRISTOL COTHAM HILL / HAMPTON PARK | 102255 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5612074460 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2017 - full year data expected | 38 | 42 | 35 | 50 | 80.1667 | 99.9911 | 34.1429 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16314C | BRISTOL BROOK ROAD / WHITEFIELD ROAD | 101791 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST5611874456 | GB530905415405 | BRISTOL AVON | RIVER AVON (ESTUARINE) VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 10 | 10 | 14 | 20 | 2.6333 | 95.7816 | 13.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16316C | BRISTOL BUDE AVENUE FOOTBALL PITCH | 102877 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST5611874456 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2018 - full year data expected | 22 | 20 | 3 | 2 | 0.16667 | 89.9806 | 11.75 | 5 (installed 2018) | Sensor failure / issue | Resolved - Aug | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16323C | BRISTOL HILLBURN ROAD / AVENING ROAD | 101794 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST5611874456 | GB530905415405 | BRISTOL AVON | RIVER AVON (E) VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 22 | 54 | 66 | 118 | 247.2 | 99.9745 | 65 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16326C | BRISTOL HUDDS VALE ROAD / PLUMERS HILL | 103311 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST5612274459 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2021 - full year data expected |  | 28 | 4 | 38 | 17.75 | 99.9829 | 23.3333 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16334C | BRISTOL NEW QUEEN ST O/S NO 72 | 101795 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST5611874456 | GB530905415405 | BRISTOL AVON | RIVER AVON (E) VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 26 | 14 | 8 | 8 | 0.73333 | 95.3695 | 14 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16335C | BRISTOL HOLDENHURST ROAD / BROAD ROAD | 102881 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST5611874456 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2018 - full year data expected | 17 | 21 | 16 | 21 | 3.1333 | 95.8733 | 18.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16336C | BRISTOL QUEEN STREET O/S NO 2 | 101796 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST5611874456 | GB530905415405 | BRISTOL AVON | RIVER AVON (E) VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 43 | 41 | 28 | 39 | 19.5 | 94.3307 | 37.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16338C | BRISTOL SALISBURY AVE O/S NO 30 | 103314 | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol East Boro Const | ST5611874456 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 31 | 17 | 11 | 21 | 2.5333 | 99.7287 | 20 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16343C | BRISTOL ST GEORGES PARK NORTH 329 CHURCH ROAD | 102884 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST5611874456 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 12 | 14 | 9 | 9 | 1.4 | 99.7763 | 11 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16347C | BRISTOL WHITEWAY ROAD O/S NO 67 | 101798 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST5611874456 | GB530905415405 | BRISTOL AVON | RIVER AVON (E) VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 40 | 43 | 28 | 56 | 32.6667 | 99.8166 | 41.75 | 5 (installed 2018) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16354C | BRISTOL MINA ROAD O/S NO 212 | 101850 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5612074460 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2019 - full year data expected | 49 | 45 | 43 | 58 | 152.1667 | 99.9981 | 39.8571 | 4 (installed 2019) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16355C | BRISTOL MULLER ROAD ALLOTMENTS | 101727 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST6013875495 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | BOILING WELLS LANE STREAM |  |  |  |  | Commissioned in 2021 - full year data expected |  | 35 | 20 | 25 | 17.5167 | 99.8298 | 26.6667 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16369C | BRISTOL CHERINGTON ROAD O/S NO 2 | 100467 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5815677315 | GB109053027530 | Trym - source to conf R Avon (Brist) | TRIB OF RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2017 - full year data expected | 52 | 44 | 39 | 57 | 124.8333 | 99.9789 | 48 | 6 (installed 2017) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2023-09-25 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16380C | BRISTOL HENLEAZE ROAD / WANSCOW WALK | 100477 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5801977358 | GB109053027530 | Trym - source to conf R Avon (Brist) | TRIB OF RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected |  | 5 | 14 | 21 | 6.7333 | 93.9167 | 13.3333 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16401C | BRISTOL TRYM ROAD O/S NO 41 | 100847 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5740977432 | GB109053027530 | Trym - source to conf R Avon (Brist) | RIVER TRYM |  |  |  |  | Commissioned in 2019 - full year data expected | 30 | 30 | 26 | 39 | 86.9167 | 100 | 31.25 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16405C | BRISTOL WELLINGTON HILL WEST NO 158 | 100466 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5815577315 | GB109053027530 | Trym - source to conf R Avon (Brist) | TRIB OF RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 60 | 48 | 46 | 67 | 208.4167 | 99.9174 | 55.25 | 4 (installed 2019) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2022-10-04 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16407C | BRISTOL WELLINGTON HILL WEST / BISHOPTHORPE ROAD | 100464 | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol North West Boro Const | ST5815577315 | GB109053027530 | Trym - source to conf R Avon (Brist) | TRIB OF RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected | 53 | 55 | 49 | 78 | 112.3333 | 99.9971 | 58.75 | 3 (installed 2020) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2018-07-05 | No sewage litter or sewage fungus | [6 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16410C | BRISTOL WESTBURY ROAD / GRANGE COURT ROAD | 013108 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5673777541 | GB109053027530 | Trym - source to conf R Avon (Brist) | RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 23 | 31 | 25 | 36 | 15.3333 | 99.0915 | 28.75 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16414C | BRISTOL AVONMOUTH ROAD / WEST TOWN ROAD | 102073 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5202277004 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2019 - full year data expected | 21 | 27 | 17 | 44 | 356.3333 | 99.5909 | 15.5714 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16422C | BRISTOL NEATH ROAD / WHITEHALL ROAD | 101799 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5611874456 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2018 - full year data expected | 7 | 22 | 20 | 33 | 16.1 | 87.2226 | 20.5 | 5 (installed 2018) | Sensor failure / issue | Resolved - Jul | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16434C | BRISTOL AVONMOUTH ROAD / WEST TOWN ROAD | 102091 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5202277004 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2019 - full year data expected | 34 | 45 | 31 | 52 | 16.6167 | 99.9907 | 40.5 | 4 (installed 2019) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13074B | COMBWICH QUAY ROAD | 103336 | Other storm discharge asset type |  | Diluted | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST2620742189 | GB540805210900 | PARRETT | RIVER PARRETT ESTUARY |  |  |  |  | Commissioned in 2018 - full year data expected | 17 | 28 | 16 | 54 | 452.85 | 100 | 19.8333 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB540805210900 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16469C | BRISTOL HANHAM LOWER HANHAM ROAD | 101759 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6289872188 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON (VIA SWS) |  |  |  |  | Commissioned in 2018 - full year data expected | 46 | 37 | 41 | 46 | 35.8333 | 95.0791 | 30 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2021-05-09 | No sewage litter or sewage fungus |  | N/A |  |  |  | No sewage fungus assessment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16470C | BRISTOL HANHAM POLLY BARNES HILL | 101750 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6289672187 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON (VIA SWS) |  |  |  |  | Commissioned in 2016 - full year data expected | 88 | 58 | 55 | 86 | 137.2833 | 99.9475 | 65.625 | 7 (installed 2016) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2019-05-24 | No sewage litter or sewage fungus | 2019-05-24 | Lab assessment - No impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16498C | COLEFORD KINGS HEAD | 103442 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Somerton and Frome Co Const | ST6880848710 | GB109053022020 | Mells source to conf with Somerset Frome | MELLS STREAM |  |  |  |  | Commissioned in 2018 - full year data expected | 49 | 34 | 36 | 52 | 170.4167 | 93.653 | 38 | 5 (installed 2018) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022020 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16502C | FROME LOWER KEYFORD | 101595 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Somerton and Frome Co Const | ST7772547081 | GB109053022101 | Frome (Maiden Bradley to Mells) | TRIB OF RIVER FROME (VIA SWS) |  |  |  |  | Commissioned in 2018 - full year data expected | 65 | 49 | 55 | 74 | 135.2667 | 100 | 50 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2020-03-26 | Sewage litter present, no sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022101 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16509C | FROME ADDERWELL CLOSE | 100444 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Somerton and Frome Co Const | ST7824747177 | GB109053022101 | Frome (Maiden Bradley to Mells) | RIVER FROME (VIA SWS) |  |  |  |  | Commissioned in 2018 - full year data expected | 65 | 55 | 56 | 69 | 157.3333 | 92.1492 | 55.875 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2020-03-26 | Sewage litter present, no sewage fungus | 2020-03-26 | Lab assessment - Impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022101 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16587C | CHIPPENHAM MONKTON PARK OFFICES | 102551 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | Chippenham Co Const | ST9208673526 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 11 | 5 | 14 | 16 | 75.9 | 99.7549 | 11.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16643C | SALISBURY ENDLESS LANE/SCOTS LANE | 043196 | SO on sewer network |  | Diluted | Rainwater | SALISBURY | Salisbury Co Const | SU1512529408 | GB108043015840 | Hampshire Avon (Lower) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected | 28 | 45 | 19 | 33 | 17.0833 | 99.9823 | 25 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015840 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16646C | SALISBURY BRIDGE STREET/HIGH STREET | 043197 | SO on sewer network |  | Diluted | Rainwater | SALISBURY | Salisbury Co Const | SU1512429408 | GB108043015840 | Hampshire Avon (Lower) | RIVER AVON VIA SW SEWER |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 8 | 22 | 29.7667 | 100 | 15 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015840 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16651C | MERE STW ADJ TO | 401438 | SO on sewer network |  | Diluted | Rainwater | SALISBURY | South West Wiltshire Co Const | ST8151231822 | GB108043022450 | Shreen Water (including Ashfield Water) | SHREEN WATER |  |  |  |  | Commissioned in 2017 - full year data expected | 45 | 39 | 30 | 68 | 86.0831 | 98.0812 | 44.8571 | 6 (installed 2017) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022450 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16655C | TISBURY NADDER CLOSE PLAYING FIELDS | 401794 | SO on sewer network |  | Diluted | Rainwater | SALISBURY | South West Wiltshire Co Const | ST9465729299 | GB108043016200 | Nadder (Upper) | RIVER NADDER VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 34 | 29 | 32 | 52 | 68.2667 | 99.9922 | 29.8571 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016200 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16674C | ILMINSTER STATION ROAD NO 37 | 102601 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST3529414852 | GB108052015190 | Isle - Upper to conf Cad Bk | SHUDRICK STREAM |  |  |  |  | Commissioned in 2018 - full year data expected | 1 | 4 | 10 | 27 | 41.5 | 99.9677 | 10.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015190 | Yes |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16760C | SALTFORD O/S 46 HIGH STREET | 013091 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6878067340 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON (VIA SWS) |  |  |  |  | Commissioned in 2018 - full year data expected | 62 | 49 | 45 | 64 | 85.5 | 96.5594 | 42 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2020-10-23 | Sewage litter present, no sewage fungus | 2020-10-23 | Lab assessment - No impact | 2022-03-01 | Water Quality Modelling shows that the WFD Status Class at the 99%ile level for BOD and Ammonia is High ‘with’ or ‘without’ all Bath FSOs |  | RICT analysis complete (No Impact) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16778C | RADSTOCK SOMERVALE ROAD REAR KHANDALLA WELTON ROAD | 021352 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6827454813 | GB109053022250 | Wellow Bk - source to conf Snails Bk | WELLOW BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 48 | 41 | 40 | 51 | 33.4333 | 98.8455 | 59.8 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2022-04-01 | Sewage litter present, no sewage fungus | 2022-04-01 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022250 | Yes |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16799C | DORCHESTER LITTLE BRITTAIN ADJ SCOUT HUT | 400690 | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | SY7085090330 | GB108044009692 | Frome Dorset (Lower) d/s Louds Mill Dorchester | (S) MILL STREAM |  |  |  |  | Commissioned in 2018 - full year data expected | 31 | 6 | 10 | 39 | 516.25 | 99.9459 | 21.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009692 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16838C | PORTISHEAD PORTBURY DITCH OFF HARBOUR RD | 102658 | SO on sewer network |  | Diluted | Rainwater | NORTH SOMERSET | North Somerset Co Const | ST4720076480 | GB109052027330 | Portbury Ditch - source to conf R Severn Estuary | PORTBURY DITCH(S) |  |  |  |  | Commissioned in 2019 - full year data expected | 22 | 17 | 1 | 18 | 59.6892 | 81.1289 | 13.4 | 4 (installed 2019) | Capital / maintenance works affect EDM operation | Resolved - Mar | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052027330 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16839C | WYKE REGIS DONCASTER ROAD | 401193 | SO on sewer network |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6713077010 | GB680805270000 | Portland Harbour | PORTLAND HARBOUR (C) | PORTLAND NORTH EASTERN BREAKWATER | PORTLAND HARBOUR CASTLE COVE/PORTLAND HARBOUR SANDSFOOT CASTLE** | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=castle%20co&site=ukk2206-20800 | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=sandsf&site=ukk2206-20900 | Commissioned in 2016 - full year data expected | 5 | 6 | 6 | 11 | 8.5226 | 99.886 | 6 | 7 (installed 2016) | [5 empty] | 2023-10-04 | Sea outfall - N/A |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB680805270000 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16847C | WEYMOUTH CHICKERELL ROAD BOYS CLUB | 400897 | SO on sewer network |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6758078730 | GB510804415700 | WEY | WEYMOUTH HARBOUR(E) | PORTLAND NORTH EASTERN BREAKWATER |  |  |  | Commissioned in 2019 - full year data expected | 8 | 11 | 13 | 22 | 5.3667 | 99.4737 | 7.7143 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB510804415700 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16886C | WATCHET MILL STREET SO | 101271 | SO on sewer network |  | Diluted | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | ST0702043370 | 421 | Not part of a river WB catchment | (S) WASHFORD RIVER |  |  |  |  | Commissioned in 2018 - full year data expected | 75 | 58 | 60 | 54 | 27.5333 | 76.6016 | 66 | 5 (installed 2018) | Sensor failure / issue | Resolved - Sep | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2021-05-21 | No sewage litter or sewage fungus | 2021-05-21 | TRAC site - N/A |  |  |  |  | Not part of a river WB catchment | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16889C | PORLOCK SO | 100354 | SO on sewer network |  | Diluted | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | SS8835047490 | GB108051020300 | Hawcombe STR | HAWKCOMBE STREAM(S) |  | PORLOCK WEIR | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=porlo&site=ukk2305-34900 |  | Commissioned in 2018 - full year data expected | 18 | 16 | 1 | 22 | 3.7333 | 99.5342 | 9.5714 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108051020300 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16894C | MINEHEAD BLENHEIM ROAD O/S COASTGUARD COTTAGES | 101774 | SO on sewer network |  | Diluted and partially treated | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | SS9727047320 | GB640807670000 | Bristol Channel Inner South | BRISTOL CHANNEL (C) |  | MINEHEAD TERMINUS | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=mineh&site=ukk2305-35000 |  | Commissioned in 2016 - full year data expected | 17 | 16 | 9 | 14 | 26.5964 | 99.9912 | 12.5 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB640807670000 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16916C | MELKSHAM BATH ROAD OFF ROAD F/O SCOUT HALL | 100630 | SO on sewer network |  | Diluted | Rainwater | WEST WILTSHIRE | Chippenham Co Const | ST9044164111 | GB109053021920 | Clackers Bk - source to conf R Avon (Brist) | CLACKERS BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 43 | 51 | 48 | 83 | 973 | 99.9409 | 48.5714 | 6 (installed 2017) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2022-05-09 | No sewage litter or sewage fungus | 2022-05-09 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021920 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16947C | CHIPPENHAM HIGH STREET O/S 6 | 103293 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | Chippenham Co Const | ST9197073360 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | RIVER AVON(S) |  |  |  |  | Commissioned in 2019 - full year data expected | 47 | 49 | 46 | 69 | 148.3333 | 99.9844 | 52.75 | 4 (installed 2019) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17058C | WRINGTON WILTONS INLET | 102486 | Inlet SO at WwTW |  | Diluted | Rainwater | NORTH SOMERSET | North Somerset Co Const | ST4649062634 | GB109052021640 | Yeo - source to conf Congresbury Yeo | TRIB OF CONGRESSBURY YEO(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 17 | 8 | 1 | 27 | 398.2 | 83.411 | 13.25 | 5 (installed 2018) | Capital / maintenance works affect EDM operation | Resolved - May | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021640 | Yes |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17166C | BATH BEWDLEY ROAD | NPSWQD002415 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7536064290 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 19 | 16 | 8 | 15 | 5.7333 | 97.2021 | 17.3333 | 5 (installed 2018) | [5 empty] | 2018-02-05 | No sewage litter or sewage fungus | [5 empty] | No sewage fungus assessment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17172C | BATH BRASSMILL LANE OPP NO 22 | 102782 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7241064930 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 37 | 17 | 27 | 34 | 218.6667 | 97.4353 | 23.2857 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17212C | FORDINGBRIDGE SALISBURY STREET | 401949 | SO on sewer network |  | Diluted | Groundwater | NEW FOREST | New Forest West Co Const | SU1500014360 | GB108043015840 | Hampshire Avon (Lower) | RIVER AVON(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 70 | 33 | 19 | 82 | 1413.3797 | 99.9115 | 51 | 5 (installed 2018) |  |  | Performance - GW inundation | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015840 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17336C | HANHAM ANSTEYS ROAD | 103355 | SO on sewer network |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6346071800 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON(E) |  |  |  |  | Commissioned in 2018 - full year data expected | 22 | 21 | 14 | 26 | 17.25 | 100 | 20.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17511C | BATH NEWBRIDGE ROAD R/O NO 131 | 102919 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7241064930 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 70 | 50 | 45 | 59 | 40.0833 | 99.99 | 56 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2022-09-26 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17512C | BATH LOCKSBROOK ROAD R/O NO 10 | EPRJB3798AB | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7345964995 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected |  | 23 | 14 | 21 | 5.9333 | 99.855 | 19.3333 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17513C | BATH LANSDOWN LANE / HIGH STREET JUNCTION WESTON | 012179 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7349865042 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 32 | 28 | 24 | 29 | 83.7667 | 96.0902 | 22.6 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17514C | BATH SOUTHLANDS RO NO 125 | 012181 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7345964995 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 38 | 21 | 1 | 1 | 0.066667 | 98.6119 | 15.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17515C | BATH WESTON VILLAGE SEWER | 012182 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7347065020 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 65 | 52 | 53 | 70 | 186.8 | 94.9753 | 59.4 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2020-11-30 | Sewage litter present, no sewage fungus |  | N/A | 2022-03-01 | Water Quality Modelling shows that the WFD Status Class at the 99%ile level for BOD and Ammonia is High ‘with’ or ‘without’ all Bath FSOs |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17517C | BATH WINDSOR COURT | 102277 | SO on sewer network |  | Diluted and partially treated | A combination of rainwater and groundwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7344364979 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2019 - full year data expected | 18 | 6 | 12 | 33 | 391.3333 | 99.9914 | 17.25 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17524C | BATH LUCKLANDS ROAD O/S LAWN COTTAGE | 012180 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7345964995 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | THE RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 29 | 20 | 17 | 29 | 5.9667 | 99.6842 | 23.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17526C | BATH UPPER BRISTOL ROAD ADJ MARLBOROUGH LANE | 010898 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7414865002 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 61 | 51 | 45 | 65 | 42.8 | 96.3702 | 55.5 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2022-03-15 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17531C | BATH GREEN PARK SYPHON INLET RIVER TOWPATH | 101191 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7485964411 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 2 | 14 | 14 | 25 | 155.6667 | 99.6925 | 13.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17532C | BATH AVON STREET O/S BATH TECHNICAL COLLEGE | 102780 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7479064440 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 54 | 36 | 40 | 66 | 108.5 | 99.9857 | 46.1667 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2020-11-30 | Sewage litter present, no sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17533C | BATH BROAD QUAY / WESTGATE STREET JUNCTION | 102783 | SO on sewer network |  | Diluted | A combination of rainwater and groundwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7504364354 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 37 | 28 | 27 | 32 | 265.3333 | 99.9033 | 31 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17534C | BATH SOUTHGATE (NORTH END) ADJ LITTLEWOODS | 102784 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7510064337 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 22 | 23 | 20 | 18 | 15.5333 | 99.6393 | 20.4 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17536C | BATH RAILWAY PLACE O/S ROYAL HOTEL | 010885 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7532164299 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2017 - full year data expected | 16 | 11 | 8 | 8 | 49.6667 | 99.9954 | 14.4 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17684C | WILLSBRIDGE | EPRMP3622XH | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6608169932 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 63 | 50 | 51 | 80 | 518.5 | 99.9743 | 61 | 5 (installed 2018) |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2019-04-20 | No sewage litter or sewage fungus | 2019-05-24 | Lab assessment - Impact |  |  |  | RICT analysis complete (LOW) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19207C | SWANAGE SHORE ROAD O/S NURSING HOME | 400033/CS/01 | SO on sewer network |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SZ0309079640 | 250 | Not part of a river WB catchment | ULWELL STREAM |  | SWANAGE CENTRAL | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=swanage&site=ukk2204-19800 |  | Commissioned in 2016 - full year data expected | 7 | 10 | 12 | 18 | 47.2489 | 99.8708 | 11.625 | 7 (installed 2016) | [13 empty] | Not part of a river WB catchment | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19280C | BRISTOL HENLEAZE ROAD JUNCTION WITH HENLEAZE PARK DRIVE | 100459 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5801877358 | GB109053027530 | Trym - source to conf R Avon (Brist) | TRIB OF THE RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 69 | 45 | 51 | 73 | 111.2 | 99.6503 | 59.5 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2023-09-25 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19292C | CHARD OLD STW BEECHING CL | 100638 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST3333909650 | GB108052015160 | Isle - Upper | TRIBUTARY OF RIVER ISLE |  |  |  |  | Commissioned in 2018 - full year data expected | 60 | 35 | 30 | 37 | 47.2001 | 99.9536 | 40.5 | 5 (installed 2018) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015160 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19308C | BRISTOL GLENWOOD ROAD SIDE OF NO 2 WESTBURY ON TRYM | 100460 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5815577315 | GB109053027530 | Trym - source to conf R Avon (Brist) | TRIBUTARY OF THE RIVER TRYM |  |  |  |  | Commissioned in 2019 - full year data expected | 58 | 47 | 39 | 65 | 125.0833 | 99.999 | 52.25 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2018-07-05 | Sewage litter present, no sewage fungus |  | N/A |  |  |  | No upstream watercourse | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19539S | BRIDPORT WYCH FARM STORM TANK | 400673 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | SY4555089120 | GB620806560000 | Lyme Bay East | LYME BAY(C) |  |  |  |  | Commissioned in 2020 - full year data expected | 58 | 52 | 40 | 70 | 535.3264 | 100 | 55 | 3 (installed 2020) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2023-10-11 | Long sea outfall - N/A |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620806560000 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19571C | CHEDDAR UNION ST JNC WITH CLIFF ST AND REDCLIFFE ST | 101662 | SO on sewer network |  | Diluted | Rainwater | SEDGEMOOR | Wells Co Const | ST4605453287 | GB109052021540 | Cheddar Yeo - source to conf Stubbingham Rhyne | CHEDDAR YEO |  |  |  |  | Commissioned in 2017 - full year data expected | 33 | 25 | 15 | 53 | 477.1333 | 99.8265 | 29.1667 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021540 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19584C | POOLE WOODLANDS AVE/HINCHLIFFE ROAD O/F | 400791 | SO on sewer network |  | Diluted | Rainwater | POOLE | Poole Boro Const | SY9978590898 | GB520804415800 | POOLE HARBOUR | HOLES BAY ESTUARINE | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA |  |  |  | Commissioned in 2016 - full year data expected | 11 | 9 | 14 | 14 | 60.2333 | 97.3817 | 7.125 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB520804415800 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19703C | BATH WELLSWAY NR 372 | NPSWQD008606 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7538564299 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 60 | 37 | 29 | 47 | 18.6333 | 99.9083 | 39.3333 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2022-03-15 | No sewage litter or sewage fungus |  | N/A | 2022-03-01 | Water Quality Modelling shows that the WFD Status Class at the 99%ile level for BOD and Ammonia is High ‘with’ or ‘without’ all Bath FSOs |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19704C | BATH BELLOTTS ROAD | 021452 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7340764927 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 29 | 27 | 23 | 30 | 17.4 | 99.9536 | 26.2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19717C | MELKSHAM SEMINGTON ROAD O/S POLICE STATION | 102323 | SO on sewer network |  | Diluted | Rainwater | WEST WILTSHIRE | Chippenham Co Const | ST8964063540 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | RIVER AVON(S) |  |  |  |  | Commissioned in 2019 - full year data expected | 51 | 20 | 23 | 33 | 136.5 | 99.9943 | 28 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19782C | BRISTOL STAPLETON ROAD R/O BLACK SWAN (UNDER FLYOVER) | 101745 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5612074460 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2018 - full year data expected | 19 | 14 | 6 | 30 | 96.0667 | 99.7549 | 13.1429 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2035 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
10944C | BRISTOL 74 BIFIELD ROAD SURFACE WATER | 011325 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6275968223 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | TRIB OF RIVER AVON VIA SWS |  |  |  |  | Sep 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
11754C | BOURNEMOUTH IFORD LANE | 041223 | SO on sewer network |  | Diluted | Rainwater | BOURNEMOUTH | Bournemouth East Boro Const | SZ1439092710 | GB520804315900 | Christchurch Harbour | RIVER STOUR |  |  |  |  | Oct 2023 |  |  |  | 6 | 14.1333 | 99.8748 |  | <1 yr (installed 2023) | [5 empty] | 2019-10-28 | No sewage litter or sewage fungus | [5 empty] | No sewage fungus assessment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB520804315900 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
12522C | POOLE HARKWOOD DRIVE 1 | 050677 | SO on sewer network |  | Diluted | Rainwater | POOLE | Poole Boro Const | SY9984091570 | GB520804415800 | Poole Harbour | HOLES BAY ESTUARINE | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA |  |  |  | Aug 2023 |  |  |  | 2 | 4.4667 | 97.6104 |  | <1 yr (installed 2023) | [5 empty] | 2020-05-22 | No sewage litter or sewage fungus | [5 empty] | Discharges into tidal saltmarsh | https://environment.data.gov.uk/catchment-planning/WaterBody/GB520804415800 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13006S | ALMONDSBURY STORM TANK | 010001 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Filton and Bradley Stoke Co Const | ST5990985033 | GB109054026650 | Chestle Pill | SANDY RHINE TRIB CHESTLE PILL |  |  |  |  | May 2023 |  |  |  | 41 | 504.45 | 99.9996 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026650 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13031S | BRADFORD-ON-AVON STORM TANK | 102190 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | Chippenham Co Const | ST8147060260 | GB109053027372 | Bristol Avon (Semington Bk to By Bk) | RIVER AVON |  |  |  |  | Commissioned in 2016 - full year data expected | 18 | 7 | 14 | 20 | 115.8333 | 99.7546 | 11 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027372 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13035S | BRINKWORTH STORM TANK | 012129 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | NORTH WILTSHIRE | North Wiltshire Co Const | SU0106383979 | GB109053027740 | Brinkworth Brook | BRINKWORTH BROOK (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 50 | 28 | 28 | 68 | 702.1667 | 99.9395 | 51.4 | 5 (installed 2018) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2021-11-17 | No sewage litter or sewage fungus | 2021-11-17 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027740 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13037S | BROADWAY OFF A358 STORM TANK | 071233 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | SOUTH SOMERSET | Yeovil Co Const | ST3323915573 | GB108052015180 | Ding | RIVER DING |  |  |  |  | Commissioned in 2018 - full year data expected | 94 | 81 | 69 | 103 | 1607.1 | 99.9235 | 86.6 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2020-10-09 | No sewage litter or sewage fungus | 2020-10-09 | Lab assessment - Impact |  |  |  | RICT analysis complete (Impact high) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015180 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13045C | CAM VALLEY DUNKERTON INLET | 102712 | Inlet SO at WwTW |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST7018658891 | GB109053022290 | Cam Bk - source to conf Wellow Bk | CAM BROOK(S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 47 | 67 | 227.8667 | 97.7823 | 57 | 1 (installed 2022) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue |  |  |  |  | 2022-03-21 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022290 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13061C | CHILCOMPTON INLET | 102218 | Inlet SO at WwTW |  | Diluted | Rainwater | MENDIP | Wells Co Const | ST6512752900 | GB109053022251 | Somer | SOMER STREAM(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 107 | 76 | 70 | 105 | 288.1667 | 96.5575 | 79.8 | 5 (installed 2018) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022251 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13076C | COMPTON DANDO INLET | 010024 | Inlet SO at WwTW |  | Diluted | A combination of rainwater and groundwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6538364552 | GB109053021950 | Chew - conf Winford Bk to conf R Avon (Brist) | BATHFORD BROOK (S) |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 129 | 133 | 1385.6333 | 99.9772 | 131 | 2 (installed 2021) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021950 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13083C | CRANMORE INLET | 102219 | Inlet SO at WwTW |  | Diluted | Rainwater | MENDIP | Somerton and Frome Co Const | ST6931443533 | GB109053021990 | Whatley Bk - source to conf Mells R | WHATLEY BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 54 | 32 | 37 | 84 | 559.7174 | 99.8773 | 51.75 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021990 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13088S | CROWCOMBE STORM TANK | 071889 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | ST1379136594 | GB108051020250 | Doniford Stream | TRIBUTARY OF DONIFORD STREAM |  |  |  |  | Commissioned in 2019 - full year data expected | 91 | 55 | 60 | 95 | 1786.5333 | 100 | 69.8 | 4 (installed 2019) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2021-05-21 | No sewage litter or sewage fungus | 2021-05-21 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108051020250 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13091S | DIDMARTON STORM TANK | 010031 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | COTSWOLD | The Cotswolds Co Const | ST8272487394 | GB109053027690 | Sherston Avon | RIVER AVON (SHERSTON BRANCH) |  |  |  |  | Commissioned in 2018 - full year data expected | 96 | 37 | 23 | 93 | 1817.5333 | 99.9041 | 62.25 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027690 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13104S | EAST CHINNOCK STORM TANK | 102510 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | SOUTH SOMERSET | Yeovil Co Const | ST4925812799 | GB108052015310 | Chinnock BK | CHINNOCK BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 75 | 54 | 44 | 71 | 607.1 | 99.8417 | 60 | 5 (installed 2018) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2020-11-17 | No sewage litter or sewage fungus |  |  |  | C Rabitti – 2 different outfalls: 1 for FE to River Avon and 1 for Storm tanks to River Marden |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015310 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13106S | EAST HARPTREE STORM TANK | 011348 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST5737256390 | GB109053021851 | Chew - source to Chew Valley Lake | TRIB OF RIVER CHEW |  |  |  |  | Commissioned in 2018 - full year data expected | 181 | 57 | 100 | 174 | 3230.9167 | 100 | 128 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2023-10-09 | No sewage litter or sewage fungus | 2023-10-09 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021851 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13121S | FARMBOROUGH STORM TANK | 102858 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6675060860 | GB109053021880 | Newton Bk - source to conf R Avon (Brist) | CONYGRE BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 64 | 38 | 42 | 69 | 1144.5 | 99.5006 | 50.3333 | 6 (installed 2017) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2021-05-14 | No sewage litter or sewage fungus | 2021-05-14 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021880 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13125S | FIVEHEAD STORM TANK | 071853 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST3642121819 | GB108052015220 | Isle - Cad Bk to Fivehead River | RIVER ISLE |  |  |  |  | Commissioned in 2018 - full year data expected | 48 | 45 | 59 | 99 | 2092.0667 | 99.8938 | 56.6 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2023-10-09 | No sewage litter or sewage fungus | 2023-10-09 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015220 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13144S | HASELBURY PLUCKNETT NEW LANE STORM TANK | 102389 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | SOUTH SOMERSET | Yeovil Co Const | ST4731011275 | GB108052015270 | Broad | SMALL BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 94 | 63 | 54 | 107 | 1751.0667 | 99.9684 | 79.5 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015270 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13146S | HAZELBURY BRYAN STORM TANK | 040037 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | NORTH DORSET | North Dorset Co Const | ST7456209339 | GB108043015940 | Lydden (Middle) | RIVER LYDDEN (S) |  |  |  |  | Commissioned in 2021 - full year data expected |  | 68 | 64 | 102 | 1959.2333 | 99.3845 | 78 | 2 (installed 2021) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015940 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13151C | HINTON ST MARY INLET | 040040 | Inlet SO at WwTW |  | Diluted | Rainwater | NORTH DORSET | North Dorset Co Const | ST7974116121 | GB108043016051 | Stour (Middle u/s Pimperne Brook) | TRIB OF CHIVERICKS BROOK |  |  |  |  | Commissioned in 2020 - full year data expected |  | 38 | 46 | 53 | 22.7667 | 99.8311 | 45.6667 | 3 (installed 2020) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016051 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13162C | ILTON ASHFORD FARM (NEAR) INLET | 072493 | Inlet SO at WwTW |  | Diluted | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST3578018530 | GB108052015220 | Isle - Cad Bk to Fivehead River | TRIBUTARY OF THE RIVER ISLE |  |  |  |  | Commissioned in 2019 - full year data expected | 48 | 44 | 56 | 70 | 612.684 | 99.9992 | 54.5 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2019-11-04 | Sewage litter present, no sewage fungus | 2019-11-04 | Field based assessment - No impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015220 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13171Z | KINGSTON SEYMOUR | 101049 | Other storm discharge asset type - with treatment |  | Diluted | Rainwater | NORTH SOMERSET | North Somerset Co Const | ST3840568661 | GB530905415401 | Severn Lower | (E) SEVERN ESTUARY |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 18 | 49 | 235.4731 | 99.9999 | 33.5 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415401 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13180C | LONG DEAN INLET | 010054 | Inlet SO at WwTW |  | Diluted | Groundwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST8478475624 | GB109053027480 | By Brook (Broadmead Bk to Doncombe Bk) | BY BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 78 | 33 | 27 | 76 | 1214.85 | 99.7905 | 61 | 6 (installed 2017) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2020-03-27 | No sewage litter or sewage fungus | 2020-03-27 | Lab assessment - No impact |  |  |  | RICT analysis complete (No Impact) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027480 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13188C | LYDLINCH INLET | 040862 | Inlet SO at WwTW |  | Diluted | Rainwater | NORTH DORSET | North Dorset Co Const | ST7502813816 | GB108043015940 | Lydden (Middle) | RIVER LYDDEN |  |  |  |  | Commissioned in 2019 - full year data expected | 82 | 68 | 61 | 86 | 533.5 | 99.5976 | 59.4 | 4 (installed 2019) |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015940 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13204S | MELKSHAM STORM TANK | 101886 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | Chippenham Co Const | ST8978063760 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | RIVER AVON |  |  |  |  | Jan 2023 |  |  |  | 45 | 788.8 | 99.594 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13208C | MERRIOTT B3165 INLET | 102289 | Inlet SO at WwTW |  | Diluted | A combination of rainwater and groundwater | SOUTH SOMERSET | Yeovil Co Const | ST4523012810 | GB108052015290 | Merriot Stream | TRIB OF GOULDS BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 41 | 49 | 42 | 67 | 291 | 99.1182 | 46.6667 | 4 (installed 2019) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015290 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13226S | NORTON ST PHILIP STORM TANK | 103269 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | MENDIP | Somerton and Frome Co Const | ST7677856130 | GB109053022260 | Lyde Bk - source to conf Wellow Bk | TRIBUTARY OF NORTON BROOK(S) |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 42 | 66 | 832.1833 | 97.9226 | 54 | 2 (installed 2021) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022260 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13227S | NUNNEY STORM TANK | 103453 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | MENDIP | Somerton and Frome Co Const | ST7363046462 | GB109053022000 | Nunney Bk - source to conf Mells R | NUNNEY BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 93 | 39 | 38 | 104 | 1771.25 | 99.8856 | 58.4 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2023-11-16 | No sewage litter or sewage fungus | 2023-11-16 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022000 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13235S | PAULTON STORM TANK | 102988 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6561657669 | GB109053022290 | Cam Bk - source to conf Wellow Bk | CAM BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 152 | 84 | 53 | 101 | 1666.4167 | 100 | 101.1667 | 6 (installed 2017) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2020-03-19 | Sewage litter present, no sewage fungus | [6 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022290 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13246S | POYNTINGTON NEAR HILLSIDE FARM STORM TANK | 071740 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | WEST DORSET | West Dorset Co Const | ST6549519640 | GB108052015630 | Yeo | RIVER YEO |  |  |  |  | Commissioned in 2018 - full year data expected | 77 | 54 | 57 | 86 | 1394.0333 | 96.6275 | 68.2 | 5 (installed 2018) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2021-05-10 | No sewage litter or sewage fungus | 2021-05-10 | Lab assessment - No impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015630 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13248S | PUCKLECHURCH STORM TANK | 010071 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST7118075713 | GB109053027510 | Boyd - source to conf R Avon (Brist) | FELTHAM BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 78 | 50 | 42 | 82 | 815.15 | 99.9893 | 69.3333 | 6 (installed 2017) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2020-05-13 | No sewage litter or sewage fungus | [6 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027510 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13292S | STOURTON CAUNDLE STORM TANK | 402296 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | NORTH DORSET | North Dorset Co Const | ST7199814587 | GB108043015960 | Caundle Brook (Lower) | CAUNDLE BROOK |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 40 | 67 | 1330.25 | 100 | 53.5 | 2 (installed 2021) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015960 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13297C | STURMINSTER NEWTON OPP RIXON CLOSE INLET | NPSWQD008026 | Inlet SO at WwTW |  | Diluted | Rainwater | NORTH DORSET | North Dorset Co Const | ST7996413981 | GB108043016051 | Stour (Middle u/s Pimperne Brook) | RIVER STOUR |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 20 | 19 | 12.9333 | 99.8933 | 19.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016051 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13304S | TARRANT CRAWFORD STORM TANK | 042479 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | NORTH DORSET | North Dorset Co Const | ST9148802976 | GB108043016052 | Stour (Middle d/s Pimperne Brook) | STOUR (S) |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 10 | 41 | 817.25 | 100 | 25.5 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016052 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13307C | TETBURY INLET | 102818 | Inlet SO at WwTW |  | Diluted | A combination of rainwater and groundwater | COTSWOLD | The Cotswolds Co Const | ST8955292456 | GB109053027800 | Tetbury Avon - source to conf unnamed trib | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 122 | 86 | 69 | 77 | 431.05 | 95.445 | 84.5 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027800 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13325S | WARMINSTER STORM TANK | 402466 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8742043670 | GB108043022520 | Wylye (Headwaters) | RIVER WYLYE |  |  |  |  | Commissioned in 2017 - full year data expected | 6 | 6 | 10 | 38 | 252.3167 | 100 | 11 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022520 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13355C | WIVELISCOMBE STYLES INLET | 102050 | Inlet SO at WwTW |  | Diluted | A combination of rainwater and groundwater | TAUNTON DEANE | Taunton Deane Co Const | ST0842028330 | GB108052015510 | Hillfarrance Bk | TRIB OF HILLFARRANCE BROOK(S) |  |  |  |  | Commissioned in 2020 - full year data expected | 36 | 58 | 57 | 80 | 106.5667 | 99.7686 | 57.75 | 3 (installed 2020) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015510 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13355S | WIVELISCOMBE STYLES STORM TANK | 102050 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | TAUNTON DEANE | Taunton Deane Co Const | ST0842028330 | GB108052015510 | Hillfarrance Bk | TRIB OF HILLFARRANCE BROOK(S) |  |  |  |  | Commissioned in 2020 - full year data expected | 120 | 90 | 77 | 145 | 2279.6333 | 99.9247 | 108 | 3 (installed 2020) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2023-09-05 | No sewage litter or sewage fungus | 2023-09-05 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015510 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13358B | WOOKEY INLET | 070130 | Inlet SO at WwTW |  | Diluted | A combination of rainwater and groundwater | MENDIP | Wells Co Const | ST5075545603 | GB109052021520 | Axe - source to Cocklake | RIVER AXE |  |  |  |  | Commissioned in 2018 - full year data expected | 21 | 23 | 1 | 20 | 187.5667 | 99.8565 | 14.4 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021520 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13368B | YEOVIL WITHOUT OFF STONE LANE INLET | 071670 | Inlet SO at WwTW |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5607018720 | GB108052015610 | Bearley Brook | TRIBUTARY OF THE BEARLEY BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 41 | 75 | 304.4167 | 99.969 | 58 | 1 (installed 2022) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015610 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13368S | YEOVIL WITHOUT OFF STONE LANE STORM TANK | 071670 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5607018720 | GB108052015610 | Bearley Brook | TRIBUTARY OF THE BEARLEY BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 42 | 74 | 885.8603 | 99.9418 | 58 | 1 (installed 2022) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015610 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14016B | BRISTOL ASHTON AVENUE | 102970 | Storm discharge at pumping station |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST5689072030 | GB530905415405 | BRISTOL AVON | RIVER AVON |  |  |  |  | Commissioned in 2020 - full year data expected | 55 | 35 | 33 | 52 | 152.45 | 99.0911 | 43.75 | 3 (installed 2020) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  |  |  | 2018-02-21 | Inaccessible |  |  |  | High tide - all submerged | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14142B | MINETY STATION ROAD | CSSA.2213 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | NORTH WILTSHIRE | North Wiltshire Co Const | SU0324090560 | GB106039023620 | Derry Brook | UNNAMED TRIB OF DERRY BROOK |  |  |  |  | Commissioned in 2020 - full year data expected | 93 | 52 | 44 | 80 | 1144.4167 | 100 | 57.8333 | 3 (installed 2020) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2023-03-09 | No sewage litter or sewage fungus | 2023-03-09 | Too deep to get samples |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB106039023620 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14152B | BROADS GREEN | 101985 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9877067510 | GB109053022040 | Willow Brook (Bristol Avon and North Somerset) | TRIB OF RIVER MARDEN(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 161 | 96 | 66 | 109 | 2158.25 | 99.9769 | 108 | 5 (installed 2018) |  |  | Performance - GW inundation | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2018-11-13 | No sewage litter or sewage fungus | 2018-11-13 | Lab assessment - No impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022040 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14161B | COMPTON BASSETT THE POND | 103449 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | NORTH WILTSHIRE | North Wiltshire Co Const | SU0331072880 | GB109053027600 | Abberd Bk - source to conf R Marden | TRIBUTARY OF ABBERD BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 140 | 84 | 24 | 133 | 2700.2667 | 99.8623 | 95.25 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2023-05-30 | No sewage litter or sewage fungus |  | N/A | 2022-06-01 | No access |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027600 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14176B | KINGTON LANGLEY | 101694 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9155076860 | GB109053027700 | Sutton Benger Bk - source to conf R Avon (Brist) | TRIB OF RIVER AVON(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 61 | 27 | 37 | 68 | 997.15 | 99.9631 | 48.2 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2023-05-02 | No sewage litter or sewage fungus | 2023-05-02 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027700 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14179B | BIDDESTONE MANOR COTTAGES | 102548 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST8670073060 | GB109053027410 | Pudding Bk - source to conf R Avon (Brist) | TRIB OF PUDDING BROOK (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 111 | 35 | 50 | 100 | 711.2331 | 99.9229 | 74 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2018-11-13 | No sewage litter or sewage fungus | 2018-11-13 | Lab assessment - Impact | 2023-01-10 | Ammonia 0.48mg/l |  | Outfall active on visit, only POI accessible | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027410 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14188B | LOWER STANTON ST QUINTIN | EPRAB3098VQ | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9160880398 | GB109053027720 | Rodbourne Bk - source to conf R Avon (Brist) | RODBOURNE BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 41 | 56 | 83 | 34 | 186.1603 | 100 | 53.5 | 5 (installed 2018) |  |  | Performance - GW inundation | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | 2022-10-11 | No sewage litter or sewage fungus | 2022-10-11 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027720 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14200B | LEA LEA NORTH | 101677 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9630086980 | GB109053027760 | Woodbridge Bk - source to conf Charlton Str | WOODBRIDGE BROOK (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 73 | 44 | 43 | 86 | 1178 | 99.9515 | 61.5 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2023-03-09 | No sewage litter or sewage fungus | 2023-03-09 | Too deep to get samples |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027760 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14202C | HANKERTON HANKERTON BRIDGE | CSSA.2214 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9690091000 | GB106039023700 | Swill Brook (source to Ashton Keynes) | UNNAMED DITCH TRIB OF BRAYDON |  |  |  |  | Commissioned in 2019 - full year data expected | 68 | 43 | 39 | 78 | 1334.3833 | 99.9888 | 50.8333 | 4 (installed 2019) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2023-03-09 | No sewage litter or sewage fungus | 2023-03-09 | TBC | 2022-04-14 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB106039023700 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14272B | BRIANTSPUDDLE | 041980 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | PURBECK | South Dorset Co Const | SY8207093220 | GB108044010080 | Piddle (Lower) | TRIBUTARY OF RIVER PIDDLE (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 14 | 11 | 2 | 9 | 58 | 100 | 9 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010080 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14288B | MARSTON MAGNA CHURCH LANE | 101772 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST5938022370 | GB108052015620 | Corton Denham Stream | RIVER YEO (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 56 | 53 | 31 | 75 | 1255.4667 | 99.9985 | 53.75 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2023-11-06 | No sewage litter or sewage fungus | 2023-11-06 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015620 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14291B | WEST CAMEL | 101764 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST5753024600 | GB108052015650 | Cam - Lower | RIVER CAM (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 61 | 55 | 38 | 82 | 1709 | 99.7546 | 59 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | 2023-03-10 | No sewage litter but light sewage fungus | 2023-03-10 | TBC | 2022-06-22 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015650 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14317B | HURDCOTT | 401575 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | SALISBURY | Salisbury Co Const | SU1690033770 | GB108043022390 | Bourne (Hampshire Avon) | RIVER BOURNE(S) |  |  |  |  | Commissioned in 2017 - full year data expected | 22 | 0 | 12 | 19 | 290.75 | 98.6102 | 13.25 | 6 (installed 2017) | [9 empty] | 2022-12-29 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022390 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14354B | BARFORD ST MARTIN | 050763 | Storm discharge at pumping station |  | Diluted | Groundwater | SALISBURY | South West Wiltshire Co Const | SU0570431168 | GB108043022470 | Nadder (Middle) | RIVER NADDER |  |  |  |  | Commissioned in 2019 - full year data expected | 34 | 5 | 0 | 11 | 183.5667 | 99.9996 | 13 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022470 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14362B | CHILMARK | 041188 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SALISBURY | South West Wiltshire Co Const | ST9708732049 | GB108043022470 | Nadder (Middle) | TRIB OF THE RIVER NADDER |  |  |  |  | Dec 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022470 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14372B | WEST HUNTSPILL SLOWAY LANE | 100880 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST2912045660 | GB540805210900 | PARRETT | (E) RIVER PARRETT |  | BURNHAM JETTY NORTH | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=burnh&site=ukk2302-35300 |  | Commissioned in 2016 - full year data expected | 5 | 7 | 4 | 7 | 36.8924 | 100 | 12.625 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB540805210900 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14374Z | HIGHBRIDGE NEWTON STORM TANKS | 102480 | Other storm discharge asset type |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Wells Co Const | ST3115047340 | GB540805210900 | PARRETT | RIVER BRUE (E) |  | BURNHAM JETTY NORTH | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=burnh&site=ukk2302-35300 |  | Commissioned in 2016 - full year data expected | 9 | 7 | 12 | 24 | 45.7208 | 98.8635 | 12.625 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB540805210900 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14404B | BEAMINSTER SOUTHGATE | 401557 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | WEST DORSET | West Dorset Co Const | ST4791700952 | GB108044009600 | Brit (Upper) | RIVER BRIT |  |  |  |  | Commissioned in 2017 - full year data expected | 72 | 56 | 43 | 79 | 808.25 | 99.9886 | 67.1667 | 6 (installed 2017) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2020-05-01 | Sewage litter present, no sewage fungus | 2020-05-01 | Lab assessment - Impact | 2022-03-01 | Water Quality Modelling shows that the WFD Status Class at the 99%ile level for BOD and Ammonia is High ‘with’ or ‘without’ all Bath FSOs |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009600 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14411B | SYDLING ST NICHOLAS | 401196 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | WEST DORSET | West Dorset Co Const | SY6322798911 | GB108044009700 | Sydling Water | TRIBUTARY OF SYDLING WATER |  |  |  |  | Commissioned in 2019 - full year data expected | 25 | 1 | 7 | 37 | 645.5 | 99.9668 | 17.5 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009700 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14414B | CHARMINSTER NORTH STREET | 402447 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | SY6665092620 | GB108044009691 | Frome Dorset (Lower) u/s Louds Mill Dorchester | THE RIVER FROME |  |  |  |  | Nov 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [9 empty] | 2022-06-30 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009691 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14426B | PAULTON GOOSARD BRIDGE | 102216 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6550157716 | GB109053022290 | Cam Bk - source to conf Wellow Bk | CAM BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 62 | 51 | 51 | 62 | 312.1667 | 99.9899 | 56.8 | 5 (installed 2018) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2021-05-14 | No sewage litter or sewage fungus | 2021-05-14 | TBC | 2021-12-13 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022290 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14428B | CORSTON NEWTON ST LOE | 010300 | Storm discharge at pumping station |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6990765557 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | CORSTON BROOK |  |  |  |  | Commissioned in 2016 - full year data expected | 61 | 39 | 39 | 65 | 248.6667 | 99.9998 | 51 | 7 (installed 2016) |  |  | Performance - Pump failure / issue | Resolved - Aug | N/A - Operational solution applied | 2023-03-21 | Sewage litter found but not sewage fungus | 2023-03-21 | TBC | 2022-01-11 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14429B | CHEW STOKE BILBIE ROAD | 021523 | Storm discharge at pumping station |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST5633761806 | GB109053021852 | Chew - Chew Valley Lake to conf Winford Brook | TRIB OF RIVER CHEW |  |  |  |  | Commissioned in 2017 - full year data expected | 1 | 31 | 21 | 47 | 62.4173 | 99.9948 | 14.2857 | 6 (installed 2017) | [9 empty] | 2021-12-09 | Impact (US 0.19mg/l, DS 0.28mg/l) |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021852 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14444B | WINGFIELD CHURCH LANE | 102026 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8257056750 | GB109053021800 | Lambrok Str - source to conf R Biss | TRIB OF LAM BROOK STREAM |  |  |  |  | Commissioned in 2018 - full year data expected | 73 | 34 | 48 | 83 | 1081.1 | 96.9711 | 59.5 | 5 (installed 2018) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021800 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14467B | HOLT THE STAR | 101024 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | Chippenham Co Const | ST8654561542 | GB109053027372 | Bristol Avon (Semington Bk to By Bk) | TRIBUTARY OF THE RIVER AVON |  |  |  |  | Commissioned in 2019 - full year data expected | 91 | 51 | 50 | 70 | 530 | 99.9971 | 61.4 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2022-05-31 | No sewage litter or sewage fungus | 2022-05-31 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027372 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14474B | MELKSHAM SEMINGTON ROUNDABOUT | 100632 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | Chippenham Co Const | ST8964063540 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | (S) RIVER AVON |  |  |  |  | Nov 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14603C | YEOVIL OLD STATION WAY | EPRTB3590ER | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5639515975 | GB108052015600 | Dodham Brook (Yeo (Somset)) | DODHAM BROOK VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  |  | 6 | 4.6333 | 99.8817 | 6 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015600 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14620B | PEWSEY SALISBURY ROAD | 041656 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | KENNET | Devizes Co Const | SU1556259354 | GB108043022410 | Hampshire Avon (East) and Woodborough Stream | RIVER AVON |  |  |  |  | Aug 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022410 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14648B | CHILTON POLDEN MAIN | 072076 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3769040420 | GB108052021181 | South Drain | NIDON BROOK (S) |  |  |  |  | Commissioned in 2020 - full year data expected | 11 | 12 | 12 | 30 | 373 | 97.9465 | 16.25 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021181 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15100B | NORTH NEWNTON | 402067 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | KENNET | Devizes Co Const | SU1356056770 | GB108043022410 | Hampshire Avon (East) and Woodborough Stream | RIVER AVON |  |  |  |  | Commissioned in 2016 - full year data expected | 29 | 11 | 3 | 33 | 478.95 | 100 | 18 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022410 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15111B | ALL CANNINGS | 401226 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | KENNET | Devizes Co Const | SU0698061810 | GB108043022430 | Etchilhampton Water | RIVER AVON (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 16 | 18 | 7 | 40 | 637.25 | 99.9914 | 20.25 | 5 (installed 2018) | [9 empty] | 2022-12-30 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022430 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15190B | MILBORNE ST ANDREW MANOR FARM | 042113 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH DORSET | North Dorset Co Const | SY8017096980 | GB108044009630 | Bere Stream | TRIBUTARY OF BERE STREAM |  |  |  |  | Commissioned in 2017 - full year data expected | 2 | 4 | 2 | 7 | 102.0983 | 98.8788 | 12.3333 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009630 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15207B | SHAFTESBURY LONG CROSS | 401300 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH DORSET | North Dorset Co Const | ST8495023250 | GB108043016100 | Key Brook | KEY BROOK TO R STOUR (S) |  |  |  |  | Commissioned in 2017 - full year data expected | 56 | 35 | 45 | 69 | 248.5 | 99.9971 | 51.25 | 6 (installed 2017) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016100 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15298B | LIMINGTON MAIN | 102569 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5390022429 | GB108052015610 | Bearley Brook | TRIB OF RIVER YEO |  |  |  |  | Commissioned in 2020 - full year data expected |  | 76 | 17 | 48 | 737.3167 | 100 | 47 | 3 (installed 2020) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue |  |  |  |  | 2022-06-22 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015610 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15299B | KINGSDON | 101845 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST5243826119 | GB108052015140 | Cary - source to conf with KSD | TRIB OF PARK BROOK |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 41 | 77 | 1581.75 | 100 | 59 | 2 (installed 2021) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015140 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15309B | CHARLTON MACKERELL ROOKERY FARM | 102064 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST5243328124 | GB108052015140 | Cary - source to conf with KSD | BULL BROOK |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 54 | 85 | 1674.9333 | 99.8421 | 69.5 | 2 (installed 2021) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015140 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15311B | YEOVIL MUDFORD | NPSWQD003764 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5748819994 | GB108052015682 | Yeo Ds Over Compton | RIVER YEO |  |  |  |  | Commissioned in 2018 - full year data expected | 9 | 12 | 10 | 11 | 90.9167 | 99.9888 | 10.4 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015682 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15313B | HUISH EPISCOPI PIBSBURY | 071157 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST4385626307 | GB108052021150 | King's Sedgemoor Drain - Henley Sluice to mouth | LONG SUTTON CATCHWATER |  |  |  |  | Commissioned in 2019 - full year data expected | 47 | 39 | 29 | 101 | 2273.75 | 99.9671 | 54 | 4 (installed 2019) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2023-11-09 | No sewage litter or sewage fungus | 2023-11-09 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021150 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15449B | MEARE GREEN WRANTAGE | 070796 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | TAUNTON DEANE | Taunton Deane Co Const | ST2979022360 | GB108052015450 | West Sedgemoor Main Drain | TRIB OF SEDGEMOOR OLD RHYNE |  |  |  |  | Commissioned in 2019 - full year data expected | 64 | 49 | 8 | 55 | 956.8667 | 99.6602 | 44 | 4 (installed 2019) |  |  | Performance - Other maintenance / capital works (e.g. jetting) | Resolved - Sep | N/A - Operational solution applied | 2023-11-04 | No sewage litter or sewage fungus | 2023-11-04 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015450 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15450B | NORTON FITZWARREN LANGFORD LANE | 101807 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | TAUNTON DEANE | Taunton Deane Co Const | ST2019027010 | GB108052021390 | Back Stream | TRIB OF RIVER TONE (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 97 | 74 | 43 | 67 | 1194.384 | 88.3907 | 70.25 | 5 (installed 2018) | Telemetry or data archiving failure / issue | Resolved - Sep | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2019-03-05 | No sewage litter or sewage fungus | 2019-03-05 | Lab assessment - Impact | 2021-11-12 | Inaccessible at time of visit |  | RICT analysis complete (LOW) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021390 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15465B | NORTH CURRY STOKE ROAD | 103190 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST3260325606 | GB108052015450 | West Sedgemoor Main Drain | TRIB OF SEDGEMOOR OLD RHYNE |  |  |  |  | Commissioned in 2020 - full year data expected |  | 42 | 40 | 52 | 464.6833 | 89.2212 | 44.6667 | 3 (installed 2020) | Sensor failure / issue | Scheduled | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue |  |  |  |  | 2022-01-17 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015450 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15468B | BRADFORD ON TONE HOCKHOLLER A38 | 070798 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | TAUNTON DEANE | Taunton Deane Co Const | ST1652721443 | GB108052015390 | Haywards Water | TRIBUTARY OF RIVER TONE |  |  |  |  | Commissioned in 2017 - full year data expected | 140 | 60 | 53 | 91 | 329.5361 | 100 | 100.1667 | 6 (installed 2017) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015390 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15505B | SYMONDSBURY WEST ROAD FOUNDRY | 402031 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | SY4546993064 | GB108044010110 | Simene | RIVER SIMENE |  |  |  |  | Commissioned in 2018 - full year data expected | 40 | 36 | 35 | 54 | 397.7667 | 100 | 46.2 | 5 (installed 2018) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2023-05-18 | No sewage litter or sewage fungus | 2023-05-18 | TBC | 2021-10-14 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010110 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15542B | KEYNSHAM HIGH LEVEL PS AVON MILL LANE | 102126 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6570568585 | GB109053021950 | Chew - conf Winford Bk to conf R Avon (Brist) | RIVER CHEW |  |  |  |  | Commissioned in 2017 - full year data expected | 58 | 38 | 44 | 56 | 153.0833 | 99.9977 | 43.8571 | 6 (installed 2017) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2022-02-28 | Sewage litter present, no sewage fungus |  | N/A |  | Very Low based on Dilution Assessment (a check Level 1 WQ model gives No Impact) |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021950 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16010C | BATH WIDCOMBE RISE OFF PRIOR PARK ROAD | 102604 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7538464298 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Mar 2023 |  |  |  | 14 | 117.2 | 99.5651 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16012C | BATH HAZEL GROVE S/O NO 22/23 | 102602 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7391065090 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON (S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  |  | 1 | 0.033333 | 99.9985 | 1 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16017C | BATH DORSET CLOSE O/S SCHOOL | 102776 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7390865093 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 13 | 10 | 6 | 7 | 0.93333 | 96.2538 | 9 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16043C | BATH RECREATION GROUND BY NORTH STAND | 102820 | SO on sewer network |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7528764882 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 89 | 62 | 48 | 69 | 263.3333 | 99.8333 | 61.25 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2018-02-05 | No sewage litter or sewage fungus |  | N/A | 2022-03-01 | Water Quality Modelling shows that the WFD Status Class at the 99%ile level for BOD and Ammonia is High ‘with’ or ‘without’ all Bath FSOs |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16068C | BATH WALCOT RIVER BANK END OF CHATHAM ROW | 101186 | SO on sewer network |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7518465425 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 63 | 50 | 42 | 51 | 116.2333 | 80.336 | 41.875 | 5 (installed 2018) | Sensor failure / issue | Resolved - Jun | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2021-03-29 | No sewage litter or sewage fungus |  | N/A | 2022-03-01 | Water Quality Modelling shows that the WFD Status Class at the 99%ile level for BOD and Ammonia is High ‘with’ or ‘without’ all Bath FSOs |  | Multiple overflows so unsuitable for invertebrate assessment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16091C | BATH ENTRY HILL GARDENS R/G NO 6 (LYNCOMBE VALE) | NPSWQD002414 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7536064290 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | THE RIVER AVON |  |  |  |  | Dec 2023 |  |  |  | 6 | 4.8 | 99.9992 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16093C | BATH LYNCOMBE VALE O/S 3 NEW VILLAS | 010935 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7538464296 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2017 - full year data expected | 12 | 14 | 5 | 5 | 1 | 99.9296 | 6.8333 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16111C | BATH WELLSWAY JUNCTION WITH KIPLING AVE | 101922 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7391065090 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON (S) |  |  |  |  | Dec 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16113C | BATH WELLSWAY R/O NO 34 | 101924 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7391065090 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Dec 2023 |  |  |  | 0 | 0 | 99.9692 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16120C | BATH WHITEWAY / RUSH HILL / ENGLISHCOMBE LANE JUNCTION | 101926 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7340864926 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | May 2023 |  |  |  | 0 | 0 | 99.9247 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16121C | BATH ENGLISHCOMBE LANE O/S 275 JUNCTION WITH MOUNT ROAD | 101927 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7340864926 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 97.4026 | 0 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16124C | BATH RUSH HILL / OLD FOSSE ROAD JUNCTION | 101930 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7343064930 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Nov 2023 |  |  |  | 0 | 0 | 99.9745 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16127C | BATH MILLMEAD ROAD NR JUNCTION LYNDHURST ROAD | NPSWQD010270 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7340664928 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | THE RIVER AVON VIA SWS |  |  |  |  | Mar 2023 |  |  |  | 0 | 0 | 99.6591 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16144C | BRISTOL STATION ROAD O/S NO 30 | 102094 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5263276269 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2018 - full year data expected | 19 | 16 | 13 | 21 | 3.5667 | 99.9346 | 17.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16175C | BRISTOL ST ANNES TERR/BRISLINGTON BROOK | 100584/CS/01 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6233672005 | GB109053021980 | Brislington Bk - source to conf R Avon (Brist) | BRISLINGTON BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 16 | 25 | 16 | 30 | 69.5 | 99.5932 | 16 | 5 (installed 2018) | [5 empty] | 2023-09-19 | No sewage litter or sewage fungus | 2023-09-19 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021980 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16194C | BRISTOL CUMBERLAND ROAD OLD GAOL SIPHON | 101080 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5856772056 | 157 | Not part of a river WB catchment | RIVER AVON VIA SWS |  |  |  |  | Aug 2023 |  |  |  | 7 | 24.7333 | 99.9661 |  | <1 yr (installed 2023) | [13 empty] | Not part of a river WB catchment | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16262C | BRISTOL BEDMINSTER ROAD SIDE OF 191 | 103305 | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol South Boro Const | ST5806872114 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 11 | 14 | 8 | 8 | 1.6333 | 99.895 | 10.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16282C | BRISTOL PEMBROKE ROAD NO 19 | 103307 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST5806772114 | 157 | Not part of a river WB catchment | RIVER AVON VIA SWS |  |  |  |  | Mar 2023 |  |  |  | 21 | 60.9 | 99.6903 |  | <1 yr (installed 2023) | [13 empty] | Not part of a river WB catchment | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16290C | BRISTOL ALMA ROAD O/S NO 87 | 102253 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5612074460 | GB530905415405 | BRISTOL AVON | RIVER AVON [BLACK ROCKS] SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 14 | 26 | 22 | 39 | 42 | 99.9896 | 20.8333 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2021-05-27 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16297C | BRISTOL CLIFTON DOWN STATION | 102254 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5612074460 | GB530905415405 | BRISTOL AVON | RIVER AVON[BLACK ROCKS](E) |  |  |  |  | Commissioned in 2017 - full year data expected | 17 | 25 | 17 | 26 | 6.5667 | 99.9847 | 21.25 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16306C | BRISTOL HAMPTON ROAD / MELVILLE COURT | 102256 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5612074460 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2017 - full year data expected | 24 | 32 | 23 | 37 | 35.75 | 100 | 22 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16318C | BRISTOL CHARLTON ROAD O/S NO 82 | 103308 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST5612074458 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 2 | 0.2 | 99.7549 | 1 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16321C | BRISTOL CONHAM VALE | 103309 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6290172188 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON (VIA SWS) |  |  |  |  | Commissioned in 2018 - full year data expected | 11 | 10 | 12 | 32 | 6.3333 | 99.9486 | 11.125 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16324C | BRISTOL HOLMES HILL ROAD OPP NO 1 | 102878 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST5612174460 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS |  |  |  |  | Mar 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16349C | BRISTOL FILTON AVENUE OUTSIDE NO 230 | 101730 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST6043976775 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | HORFIELD BROOK VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected |  | 101 | 90 | 116 | 302.9 | 99.9228 | 102.3333 | 3 (installed 2020) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" |  |  |  |  | 2022-06-01 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16372C | BRISTOL EAST HILL / CHOCK LANE | EPRSB3393AV | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5740677433 | GB109053027530 | Trym - source to conf R Avon (Brist) | RIVER TRYM VIA SWS |  |  |  |  | Dec 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [5 empty] | 2019-10-02 | No sewage litter or sewage fungus | [5 empty] | No sewage fungus assessment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16475C | BRISTOL KINGSWOOD NEW CHELTENHAM ROAD NO 170 | 100889 | SO on sewer network |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6632074370 | GB109053027450 | Siston Bk - source to conf R Avon (Brist) | WARMLEY BROOK VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 50 | 58 | 69 | 79 | 134.9667 | 99.9916 | 54.375 | 4 (installed 2019) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2020-10-29 | No sewage litter or sewage fungus |  | N/A |  |  |  | No upstream watercourse | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027450 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16481C | BRISTOL KINGSWOOD NEW CHELTENHAM ROAD O/S 43 | 100895 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6631974374 | GB109053027450 | Siston Bk - source to conf R Avon (Brist) | WARMLEY BROOK VIA SWS |  |  |  |  | Commissioned in 2021 - full year data expected |  | 47 | 47 | 70 | 83.1 | 99.9037 | 54.6667 | 2 (installed 2021) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027450 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16484C | BRISTOL KINGSWOOD ALMA ROAD / NEW CHELTENHAM ROAD JUNCTION | 100897 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6631974374 | GB109053027450 | Siston Bk - source to conf R Avon (Brist) | WARMLEY BROOK VIA SWS |  |  |  |  | Mar 2023 |  |  |  | 48 | 65.0667 | 99.6648 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027450 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16499C | CROSCOMBE FAYRE WAY / LONG | 102368 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Wells Co Const | ST5856944409 | GB108052021221 | Sheppey | RIVER SHEPPEY |  |  |  |  | Commissioned in 2018 - full year data expected | 10 | 13 | 11 | 15 | 13.3667 | 96.3383 | 9.8333 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021221 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16557C | FRAMPTON COTTERELL CLYDE ROAD BRICKENHILL PERSONAGE BRIDGE (SE) | 103071 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6656981732 | GB109053027820 | Frome (Brist) - conf Laddon Bk to conf Folly Bk | RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 46 | 39 | 40 | 59 | 171.3 | 99.8436 | 38.7143 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2021-04-13 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027820 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16577C | CHIPPENHAM GASTONS ROAD | 102550 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | Chippenham Co Const | ST9137373707 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | HARDENHUISH BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 76 | 52 | 55 | 82 | 458.3333 | 99.9943 | 66.25 | 4 (installed 2019) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16647C | SALISBURY COLLEGE STREET NO 28 | 041303 | SO on sewer network |  | Diluted | Rainwater | SALISBURY | Salisbury Co Const | SU1513029410 | GB108043015840 | Hampshire Avon (Lower) | RIVER AVON VIA SWS |  |  |  |  | Aug 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015840 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16666C | COSSINGTON BROOKHAYES | 101685 | SO on sewer network |  | Diluted | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3586040710 | GB108052021210 | Huntspill | COSSINGTON BROOK(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 29 | 53 | 27 | 71 | 86.0667 | 96.1541 | 45 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021210 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16697C | EAST COKER MOOR LANE | 102259 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5409812852 | GB108052015590 | Sutton Bingham Stream - conf Closworth Str to conf Yeo | TRIBUTARY OF RIVER YEO |  |  |  |  | Commissioned in 2020 - full year data expected | 49 | 51 | 43 | 58 | 219.3333 | 99.7222 | 50.25 | 3 (installed 2020) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015590 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16723C | WOTTON-UNDER-EDGE HACK MILL | 102083 | SO on sewer network |  | Diluted and partially treated | Rainwater | STROUD | The Cotswolds Co Const | ST7589692821 | GB109054026610 | Ozleworth Bk - source to conf Little Avon R | DYERS BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 89 | 62 | 53 | 80 | 250.9167 | 99.9529 | 71 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026610 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16753C | BATHEASTON COALPIT ROAD JUNCTION WITH LONDON ROAD | 021480 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST7805467414 | GB109053027810 | St Catherines Bk - source to conf R Avon (Brist) | ST. CATHERINES BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 64 | 38 | 38 | 69 | 487.8333 | 99.7538 | 52.25 | 5 (installed 2018) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027810 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16761C | SALTFORD WICKHOUSE FARM BATH ROAD | 102129 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6805068710 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Feb 2023 |  |  |  | 1 | 0.25 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16765C | RADSTOCK WATERSIDE SO | 021353 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6800853727 | GB109053022240 | Snails Bk - source to conf Kilmersdon Str | TRIB OF WATERSIDE |  |  |  |  | Commissioned in 2018 - full year data expected | 79 | 113 | 82 | 18 | 6.9333 | 99.6016 | 68.3333 | 5 (installed 2018) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2021-03-16 | No sewage litter or sewage fungus |  | N/A |  |  |  | Outfall not visible | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022240 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16813C | BRIDPORT SOUTH STREET DEPOT | 402084 | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | SY4645092280 | GB108044009600 | Brit (Upper) | RIVER BRIT |  |  |  |  | Commissioned in 2018 - full year data expected | 74 | 59 | 56 | 65 | 323.9667 | 82.7877 | 47.3333 | 5 (installed 2018) | Sensor failure / issue | Resolved - Jun | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009600 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16822C | BRIDPORT WEST STREET | 402083 | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | SY4632093020 | GB108044009600 | Brit (Upper) | RIVER BRIT |  |  |  |  | Commissioned in 2017 - full year data expected | 59 | 47 | 41 | 56 | 166.0667 | 99.8326 | 49 | 6 (installed 2017) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2020-11-10 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009600 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16835C | CHEW MAGNA BATTLE LANE | EPRBB3193AR | SO on sewer network |  | Diluted and partially treated | A combination of rainwater and groundwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST5686263261 | GB109053021900 | Winford Bk - source to conf R Chew | WINFORD BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 82 | 59 | 23 | 61 | 578.25 | 99.9971 | 47.6667 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2021-03-09 | Sewage litter present, no sewage fungus | 2021-03-09 | Lab assessment - Impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021900 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16849C | WEYMOUTH CRANFORD AVENUE | 401190 | SO on sewer network |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6859780667 | 427 | Not part of a river WB catchment | TRIB OF WEYMOUTH BAY (VIA SWS) |  | WEYMOUTH LODMOOR | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=lodmoor&site=ukk2206-20600 |  | Commissioned in 2018 - full year data expected | 9 | 7 | 0 | 0 | 0 | 99.8782 | 6.375 | 5 (installed 2018) | [5 empty] | 2023-10-04 | No sewage litter, but sewage fungus spotted |  | N/A |  |  |  |  | Not part of a river WB catchment | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16879C | HAWKWELL HAWKWELL SO | 070230 | SO on sewer network |  | Diluted | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | SS9259539770 | GB108051020210 | Avill | RIVER AVILL |  |  |  |  | Commissioned in 2018 - full year data expected | 106 | 92 | 86 | 134 | 302.1333 | 99.6762 | 104 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2021-05-21 | No sewage litter or sewage fungus | 2021-05-21 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108051020210 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16899C | BRADFORD-ON-AVON MARKET STREET JUNCTION WITH CHURCH STREET | 101649 | SO on sewer network |  | Diluted | Rainwater | WEST WILTSHIRE | Chippenham Co Const | ST8261260932 | GB109053027372 | Bristol Avon (Semington Bk to By Bk) | RIVER AVON (VIA SWS) |  |  |  |  | Commissioned in 2016 - full year data expected | 47 | 38 | 42 | 56 | 70 | 99.9182 | 46.125 | 7 (installed 2016) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2021-03-16 | No sewage litter or sewage fungus |  | N/A - WQM required | 2022-03-01 | Water Quality Modelling shows no impact |  | Multiple overflows so unsuitable for invertebrate assessment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027372 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16909C | MELKSHAM SHAW C OF E SCHOOL PLAYING FIELD | 102811 | SO on sewer network |  | Diluted | Rainwater | WEST WILTSHIRE | Chippenham Co Const | ST8879665886 | GB109053021930 | South Bk - source to conf R Avon (Brist) | SOUTH BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 69 | 50 | 45 | 68 | 591.5 | 99.999 | 58.8571 | 6 (installed 2017) |  |  | Performance - Other maintenance / capital works (e.g. jetting) | Resolved - Oct | N/A - Operational solution applied | 2021-05-18 | Sewage litter present, no sewage fungus | 2021-05-18 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021930 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16950C | WINTERBOURNE HARCOMBE FARM HICKS COMMON IN FIELD | 103069 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Filton and Bradley Stoke Co Const | ST6568680016 | GB109053027820 | Frome (Brist) - conf Laddon Bk to conf Folly Bk | RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 74 | 37 | 35 | 57 | 66.1667 | 99.8139 | 45.5714 | 5 (installed 2018) |  |  | Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue | Resolved - Aug | N/A - Operational solution applied | 2018-04-13 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027820 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17113C | BATH HAYCOMBE DRIVE NO 223 IN BACK GARDEN | NPSWQD008608 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7292164760 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | THE RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 4 | 1 | 0.13333 | 97.1956 | 2.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17143C | ASHILL MAIN INLET | 102972 | Inlet SO at WwTW |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST3217017880 | GB108052015241 | Fivehead River | VENNER'S WATER(S) |  |  |  |  | Feb 2023 |  |  |  | 71 | 602.2261 | 99.9682 |  | <1 yr (installed 2023) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015241 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17390C | FRESHFORD FIELDS OFF ROSEMARY LANE | 010822 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST7856659569 | GB109053021840 | Somerset Frome conf with Mells to conf B. Avo | RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 73 | 34 | 32 | 63 | 143.1667 | 99.7515 | 50.5 | 5 (installed 2018) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021840 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19031C | BUCKLAND NEWTON DUNTISH INLET | 043204 | Inlet SO at WwTW |  | Diluted | Groundwater | WEST DORSET | West Dorset Co Const | ST7008406363 | GB108043015890 | Lydden (Upper) | RIVER LYDDEN |  |  |  |  | Commissioned in 2018 - full year data expected | 97 | 123 | 107 | 145 | 2549.7 | 97.2085 | 118 | 5 (installed 2018) |  |  | Performance - Infiltration | Scheduled | Stage 1b: Confirmed "asset maintenance" issue |  |  |  |  | 2022-02-16 | No impact (US 0.19mg/l, DS 0.19mg/l) |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015890 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19538C | BATH BATHEASTON BY-PASS | 100680 | SO on sewer network |  | Diluted | A combination of rainwater and groundwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7667066483 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 87 | 54 | 53 | 95 | 995.7667 | 96.0247 | 69.7143 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2020-11-30 | Sewage litter present, no sewage fungus |  | N/A | 2022-03-01 | Water Quality Modelling shows that the WFD Status Class at the 99%ile level for BOD and Ammonia is High ‘with’ or ‘without’ all Bath FSOs |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19567C | BRISTOL CRANBROOK ROAD O/S NO.67 | 011395 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5861175071 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | CRANBROOK VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 53 | 53 | 50 | 63 | 77.75 | 99.98 | 54.75 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2023-09-28 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19697C | WATCHET MARKET ST | 101159 | Storm discharge at pumping station |  | Diluted | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | ST0700043470 | 421 | Not part of a river WB catchment | WASHFORD RIVER (E) |  |  |  |  | Commissioned in 2019 - full year data expected | 12 | 9 | 10 | 22 | 17.15 | 99.9833 | 12.4 | 4 (installed 2019) | [13 empty] | Not part of a river WB catchment | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19903C | WICK THE GREEN | 102838 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6952072600 | GB109053027510 | Boyd - source to conf R Avon (Brist) | THE RIVER BOYD (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 49 | 39 | 35 | 57 | 299 | 99.9847 | 45 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027510 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19954C | BRISTOL WORDSWORTH ROAD ATTENUATION TANK | EPRAP3923GZ | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST6043876774 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | THE HORFIELD BROOK |  |  |  |  | Mar 2023 |  |  |  | 39 | 64.3667 | 99.9962 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19965C | BRISTOL OAKLEY ROAD / FILTON AVENUE NEW | 101851 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST6044076780 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | HORFIELD BROOK (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 46 | 46 | 42 | 62 | 61.75 | 99.9981 | 49 | 5 (installed 2018) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19977C | BRISTOL MULLER ROAD R/O HORFIELD UNITED REFORM CHURCH | 101849 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5998076030 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | HORFIELD BROOK (S) |  |  |  |  | Commissioned in 2019 - full year data expected | 140 | 119 | 105 | 135 | 671.1833 | 99.9817 | 124.75 | 4 (installed 2019) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" |  |  |  |  | 2022-06-01 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19999C | WARMINSTER GEORGE ST | 401093 | SO on sewer network |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8723345172 | GB108043022540 | Wylye Trib (The Were or Swan) | THE WERE |  |  |  |  | Commissioned in 2017 - full year data expected | 2 | 1 | 1 | 0 | 0 | 99.8756 | 0.57143 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022540 | No |  |  | 2040 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
10288C | BRISTOL HARBURY ROAD | 100470 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5815577315 | GB109053027530 | Trym - source to conf R Avon (Brist) | TRIB OF RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 4 | 12 | 8 | 4 | 0.23333 | 99.9928 | 7 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
10312C | IRON ACTON HOOVERS LANE | 100985 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6694083180 | GB109053027560 | Frome (Brist) - source to conf Laddon Bk | (S) RIVER FROME |  |  |  |  | Oct 2023 |  |  |  | 39 | 378.1169 | 100 |  | <1 yr (installed 2023) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue |  |  |  |  | 2021-11-25 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027560 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
10515C | BRISTOL ROCKLAND ROAD | EPRPB3332AU | SO on sewer network |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Filton and Bradley Stoke Co Const | ST6456877019 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | LINCOMBE BARN STREAM |  |  |  |  | Sep 2023 |  |  |  | 10 | 20.5964 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
11922C | BOURNEMOUTH MAXWELL ROAD | Unpermitted | SO on sewer network |  | Diluted | Rainwater | BOURNEMOUTH | Bournemouth West Boro Const | SZ1333593666 | GB108043011040 | Stour (Lower) | Stour (Lower) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 27 | 29 | 14.7 | 99.9901 | 28 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011040 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13001S | ABBOTSBURY B3157 PORTESHAM ROAD STORM TANK | 040001 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | SY5885584921 | 2 | Not part of a river WB catchment | ABBOTSBURY BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 11 | 7 | 24 | 98 | 2014.4667 | 100 | 33.6667 | 6 (installed 2017) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | Not part of a river WB catchment | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13028S | BOWERHILL SHAILS LANE STORM TANK | 102735 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | WEST WILTSHIRE | Chippenham Co Const | ST9031162368 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | BERRYFIELD STREAM(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 41 | 21 | 35 | 60 | 773.4 | 99.9395 | 38 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13044C | CALNE INLET | 103731 | Inlet SO at WwTW |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9791071440 | GB109053022050 | Marden - source to conf Cowage Bk | RIVER MARDEN(S) |  |  |  |  | Commissioned in 2017 - full year data expected | 34 | 16 | 20 | 56 | 120.2 | 99.9994 | 26.6667 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022050 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13044S | CALNE STORM TANK | 103731 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9778071530 | GB109053022050 | Marden - source to conf Cowage Bk | RIVER MARDEN(S) |  |  |  |  | Commissioned in 2017 - full year data expected | 56 | 21 | 31 | 58 | 910.25 | 99.6832 | 40.3333 | 6 (installed 2017) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2018-05-01 | No sewage litter or sewage fungus | 2018-11-13 | Lab assessment - Impact |  |  |  | RICT analysis complete (Extremely severe) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022050 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13047S | CANNINGTON STORM TANK | 101442 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST2693039370 | GB108052021310 | Cannington Bk - Lower | CANNINGTON BROOK (S) |  |  |  |  | Commissioned in 2017 - full year data expected | 51 | 52 | 35 | 91 | 1074.5 | 99.9092 | 43.6667 | 6 (installed 2017) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2023-10-04 | No sewage litter or sewage fungus | 2023-10-04 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021310 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13055S | CHARLTON HORETHORNE MOUNT LANE STORM TANK | 072373 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST6692322583 | GB108052015630 | Yeo | BROMERS BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 25 | 13 | 20 | 33 | 365.6 | 99.5411 | 23.2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015630 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13062C | CHILTHORNE DOMER OFF VAGG LANE INLET | 070019 | Inlet SO at WwTW |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5281019250 | GB108052015610 | Bearley Brook | TRIB OF BEARLEY BROOK (S) |  |  |  |  | Commissioned in 2020 - full year data expected |  | 35 | 20 | 49 | 203.6339 | 99.9992 | 34.6667 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015610 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13069C | COLEFORD INLET | 010265 | Inlet SO at WwTW |  | Diluted | Groundwater | MENDIP | Somerton and Frome Co Const | ST6917148925 | GB109053022020 | Mells source to conf with Somerset Frome | MELLS RIVER |  |  |  |  | Commissioned in 2017 - full year data expected | 37 | 33 | 35 | 28 | 93.25 | 99.9629 | 35.3333 | 6 (installed 2017) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022020 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13073S | COMBE ST NICHOLAS OFF PUDLEIGH LANE STORM TANK | 103843 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST3196610868 | GB108052015160 | Isle - Upper | RIVER ISLE |  |  |  |  | Commissioned in 2017 - full year data expected | 9 | 8 | 4 | 3 | 15.5 | 99.9715 | 6.5 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015160 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13078S | CORFE MULLEN DORCHESTER ROAD STORM TANK | 040022 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | EAST DORSET | Mid Dorset and North Poole Co Const | SY9899699395 | GB108043016052 | Stour (Middle d/s Pimperne Brook) | RIVER STOUR |  |  |  |  | Commissioned in 2018 - full year data expected | 56 | 30 | 30 | 54 | 597.6333 | 99.8535 | 42.2 | 5 (installed 2018) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2022-09-16 | No sewage litter or sewage fungus | 2022-09-16 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016052 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13084S | CREWKERNE TRADING ESTATE CREWKERNE EAST STORM TANK | 101456 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST4508309655 | GB108052015260 | Parrett - headwaters to Broad River | CREWKERNE STREAM (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 41 | 34 | 33 | 68 | 910.4 | 99.9722 | 35.2 | 5 (installed 2018) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015260 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13090S | DEVIZES WEBBS LANE STORM TANK | 102172 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | KENNET | Devizes Co Const | ST9938561167 | GB109053022190 | Poulshot Str - source to conf Summerham Bk | WAYLEN BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 20 | 18 | 23 | 25 | 181.8517 | 99.6459 | 21.5 | 5 (installed 2018) | [5 empty] | 2023-05-10 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022190 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13092C | DILTON MARSH INLET | 010032 | Inlet SO at WwTW |  | Diluted | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8392050090 | GB109053021760 | Tributary - source to conf Biss Bk | FAIRBOURNE STREAM (S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 33 | 72 | 616.65 | 99.98 | 52.5 | 1 (installed 2022) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021760 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13098S | DOWLISH WAKE KINGSTON STORM TANK | 072317 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | SOUTH SOMERSET | Yeovil Co Const | ST3724013020 | GB108052015170 | Dowlish Brook | DOWLISH BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 32 | 35 | 4 | 23 | 131.1333 | 99.9323 | 22.4 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015170 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13105S | EAST COKER MOOR LANE STORM TANK | 071196 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5470013030 | GB108052015590 | Sutton Bingham Stream - conf Closworth Str to conf Yeo | STOFORD BROOK (S) |  |  |  |  | Commissioned in 2020 - full year data expected |  | 27 | 28 | 48 | 359 | 99.9992 | 34.3333 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015590 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13113C | EDFORD INLET | 010034 | Inlet SO at WwTW |  | Diluted | Rainwater | MENDIP | Somerton and Frome Co Const | ST6718448659 | GB109053022020 | Mells source to conf with Somerset Frome | MELLS RIVER (S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 29 | 77 | 422.6333 | 99.9349 | 53 | 1 (installed 2022) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022020 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13113S | EDFORD STORM TANK | 010034 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | MENDIP | Somerton and Frome Co Const | ST6718448659 | GB109053022020 | Mells source to conf with Somerset Frome | MELLS RIVER (S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 38 | 97 | 849.9667 | 99.9442 | 67.5 | 1 (installed 2022) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022020 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13118C | EVERCREECH INLET | 102152 | Inlet SO at WwTW |  | Diluted | A combination of rainwater and groundwater | MENDIP | Somerton and Frome Co Const | ST6456037540 | GB108052021160 | Alham | RIVER ALHAM |  |  |  |  | Commissioned in 2018 - full year data expected |  | 42 | 34 | 56 | 176.0333 | 99.9985 | 44 | 5 (installed 2018) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021160 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13118S | EVERCREECH STORM TANK | 102152 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | MENDIP | Somerton and Frome Co Const | ST6456037540 | GB108052021160 | Alham | RIVER ALHAM |  |  |  |  | Commissioned in 2020 - full year data expected | 35 | 22 | 19 | 40 | 431.0667 | 99.6465 | 29 | 3 (installed 2020) | [5 empty] | 2023-05-11 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021160 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13131S | FROME WELSHMILL LANE STORM TANKS STORM TANK | 102222 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | MENDIP | Somerton and Frome Co Const | ST7735248660 | GB109053022101 | Frome (Maiden Bradley to Mells) | RIVER FROME(S) |  |  |  |  | Commissioned in 2019 - full year data expected | 30 | 13 | 21 | 33 | 77.2333 | 99.9852 | 24.25 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022101 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13133C | GLANVILLES WOOTTON INLET | 040036 | Inlet SO at WwTW - with treatment | Reed bed | Fully treated | Rainwater | NORTH DORSET | North Dorset Co Const | ST6732308968 | GB108043015910 | Caundle Brook (Upper) | TRIB OF CAUNDLE BROOK |  |  |  |  | Commissioned in 2020 - full year data expected | 13 | 74 | 39 | 113 | 629.8833 | 76.897 | 59.75 | 3 (installed 2020) | Telemetry or data archiving failure / issue | Resolved - May | N/A - Ongoing investigation | N/A - Ongoing investigation | [8 empty] | Has wetland treatment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015910 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13150C | HINTON BLEWETT INLET | 010299 | Inlet SO at WwTW |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST5939156677 | GB109053022290 | Cam Bk - source to conf Wellow Bk | THE CAM BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 41 | 26 | 27 | 48 | 125.7 | 99.9996 | 35.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022290 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13169S | KINGS STAG STORM TANK | 040047 | Inlet SO at WwTW |  | Diluted | A combination of rainwater and groundwater | NORTH DORSET | North Dorset Co Const | ST7267810766 | GB108043015940 | Lydden (Middle) | RIVER LYDDEN |  |  |  |  | Commissioned in 2019 - full year data expected | 31 | 20 | 31 | 36 | 332.25 | 96.8864 | 24 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015940 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13181B | LONGBRIDGE FOSSE WAY INLET | 101620 | Inlet SO at WwTW |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST4181014010 | GB108052015330 | Lopen Brook | LOPEN STREAM(S) |  |  |  |  | Commissioned in 2017 - full year data expected | 43 | 36 | 2 | 4 | 25.8 | 100 | 29.5 | 6 (installed 2017) | [5 empty] | 2021-04-15 | No sewage litter or sewage fungus |  | N/A | 2022-02-17 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015330 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13184S | LUCKINGTON STORM TANK | 010156 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST8380183912 | GB109053027665 | Luckington Bk | LUCKINGTON BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 18 | 22 | 19 | 45 | 600.5333 | 100 | 25.8 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027665 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13208S | MERRIOTT B3165 STORM TANK | 102289 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | SOUTH SOMERSET | Yeovil Co Const | ST4523012810 | GB108052015290 | Merriot Stream | TRIB OF GOULDS BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 27 | 37 | 48 | 55 | 771.25 | 99.4092 | 42.1667 | 4 (installed 2019) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2020-04-03 | No sewage litter or sewage fungus | [6 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015290 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13237S | PEWSEY SALISBURY ROAD STORM TANK | 042464 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | KENNET | Devizes Co Const | SU1558559375 | GB108043022410 | Hampshire Avon (East) and Woodborough Stream | RIVER AVON (HAMPSHIRE) |  |  |  |  | Commissioned in 2019 - full year data expected | 5 | 11 | 13 | 49 | 171.9833 | 97.303 | 14.5 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022410 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13239S | PILTON STORM TANK | 070087 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | MENDIP | Wells Co Const | ST5844440511 | GB108052021173 | Whitelake | TRIBUTARY OF WHITELAKE |  |  |  |  | Commissioned in 2019 - full year data expected | 43 | 33 | 23 | 60 | 1220.5 | 91.3955 | 39.8 | 4 (installed 2019) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2022-11-16 | No sewage litter or sewage fungus | 2022-11-16 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021173 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13244S | POTTERNE STORM TANK | 102629 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | KENNET | Devizes Co Const | ST9871759139 | GB109053022190 | Poulshot Str - source to conf Summerham Bk | SEMINGTON BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 29 | 16 | 18 | 21 | 42.1333 | 99.8992 | 21 | 5 (installed 2018) | [5 empty] | 2018-11-16 | No sewage litter or sewage fungus |  |  | 2022-09-24 | Impact (US 0.56mg/l, DS 1.04mg/l) |  | Combined FE and SO | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022190 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13252A | RADSTOCK MILL LANE INLET 1 | 102630 | Inlet SO at WwTW |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6990255131 | GB109053022271 | Wellow Bk - Snails Bk to Bristol Avon | WELLOW BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 45 | 31 | 24 | 12 | 63.25 | 100 | 29.6 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022271 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13252B | RADSTOCK MILL LANE INLET 2 | 102630 | Inlet SO at WwTW |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6990555133 | GB109053022271 | Wellow Bk - Snails Bk to Bristol Avon | WELLOW BROOK |  |  |  |  | Commissioned in 2020 - full year data expected |  | 31 | 23 | 12 | 64.5 | 99.9829 | 22 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022271 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13252S | RADSTOCK MILL LANE STORM TANK | 102630 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6993355139 | GB109053022271 | Wellow Bk - Snails Bk to Bristol Avon | WELLOW BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 63 | 29 | 64 | 118 | 1487.6 | 100 | 62.6 | 4 (installed 2019) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation |  | 2022-09-27 | No sewage litter or sewage fungus | 2022-09-27 | Field based assessment - No impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022271 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13260S | SANDHILL PARK STORM TANK | 072535 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST1573229142 | GB108052021380 | Halse WTR | TRIBUTARY OF HALSE WATER |  |  |  |  | Commissioned in 2017 - full year data expected | 35 | 20 | 17 | 43 | 363 | 99.9971 | 33.3333 | 6 (installed 2017) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2022-05-31 | No sewage litter or sewage fungus | 2022-05-31 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021380 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13262S | SEEND STORM TANK | 102715 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | KENNET | Devizes Co Const | ST9538261180 | GB109053022220 | Summerham Brook | SEEND HILL STREAM(S) |  |  |  |  | Commissioned in 2019 - full year data expected | 62 | 21 | 36 | 73 | 1324.8667 | 99.1218 | 48 | 4 (installed 2019) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022220 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13263C | SEMLEY INLET | 040076 | Inlet SO at WwTW |  | Diluted and partially treated | Rainwater | SALISBURY | South West Wiltshire Co Const | ST8743826938 | GB108043016210 | Sem | TRIBUTARY OF RIVER SEM |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 20 | 15 | 17 | 99.9803 | 17.5 | 2 (installed 2021) | [5 empty] | 2021-10-15 | No sewage litter or sewage fungus | [6 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016210 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13264C | SHAFTESBURY GEARS MILL INLET | 401758 | Inlet SO at WwTW |  | Diluted | Rainwater | NORTH DORSET | North Dorset Co Const | ST8615021610 | GB108043016110 | Stirchell Brook | STIRCHELL BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 38 | 20 | 22 | 37 | 24.7667 | 99.8642 | 30.8 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016110 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13264S | SHAFTESBURY GEARS MILL STORM TANK | 401758 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | NORTH DORSET | North Dorset Co Const | ST8584021030 | GB108043016110 | Stirchell Brook | STIRCHELL BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 9 | 8 | 13 | 17 | 33.4 | 99.8467 | 11 | 5 (installed 2018) | [5 empty] | 2023-03-14 | 1 piece of sewage litter, no sewage fungus | 2023-03-14 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016110 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13267S | SHEPTON MALLET DARSHILL STORM TANK | 101543 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | MENDIP | Wells Co Const | ST6030043970 | GB108052021221 | Sheppey | RIVER SHEPPEY |  |  |  |  | Commissioned in 2017 - full year data expected | 40 | 35 | 36 | 108 | 1943.75 | 100 | 49.5 | 6 (installed 2017) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021221 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13269S | SHERSTON STORM TANK | 011559 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST8588985657 | GB109053027690 | Sherston Avon | AVON (SHERSTON BRANCH) |  |  |  |  | Commissioned in 2019 - full year data expected | 28 | 28 | 33 | 43 | 476.75 | 99.8459 | 31.6 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027690 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13281S | SOUTH PETHERTON NORTH STREET STORM TANK | 102511 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST4308017410 | GB108052015340 | Lam Brook | NORTH MILLS BROOK(S) |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 30 | 60 | 789.9667 | 100 | 45 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015340 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13286S | STANTON DREW STORM TANK | 012549 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6029463320 | GB109053021950 | Chew - conf Winford Bk to conf R Avon (Brist) | RIVER CHEW |  |  |  |  | Commissioned in 2018 - full year data expected | 45 | 20 | 7 | 38 | 662.0333 | 99.8337 | 27.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021950 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13297S | STURMINSTER NEWTON OPP RIXON CLOSE STORM TANK | NPSWQD008026 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | NORTH DORSET | North Dorset Co Const | ST7996413981 | GB108043016051 | Stour (Middle u/s Pimperne Brook) | RIVER STOUR |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 24 | 31 | 333.9333 | 69.3942 | 27.5 | 1 (installed 2022) | Sensor failure / issue | Resolved - Aug | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016051 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13306S | TEMPLECOMBE STORM TANK | 040093 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST7143222775 | GB108043015820 | Bow Brook North | THE BOW BROOK(S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 29 | 64 | 801.9497 | 99.9916 | 46.5 | 1 (installed 2022) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015820 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13312S | TINTINHULL ASH BEARLEY LANE STORM TANK | 071609 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | SOUTH SOMERSET | Yeovil Co Const | ST4897020810 | GB108052015682 | Yeo Ds Over Compton | TRIB OF WITCOMBE BOTTOM DRAIN |  |  |  |  | Commissioned in 2019 - full year data expected | 23 | 36 | 44 | 72 | 981.25 | 99.9868 | 36.7143 | 4 (installed 2019) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015682 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13314C | TOCKENHAM INLET | 010238 | Inlet SO at WwTW |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | SU0412779049 | GB109053027640 | Cowage Bk - source to conf unnamed trib | COWAGE BROOK,DITCH TRIB OF |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 30 | 77 | 445.75 | 98.7116 | 53.5 | 1 (installed 2022) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027640 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13329S | WEDMORE STORM TANK | 072054 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Wells Co Const | ST4391148071 | GB109052021570 | Axe - Cocklake to Brean Cross Sluice | TRIB OF LANDCOURSE RHYNE |  |  |  |  | Commissioned in 2017 - full year data expected | 29 | 19 | 22 | 57 | 187.9333 | 99.8912 | 31.75 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021570 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13334B | BRIDPORT WEST BAY | 400678 | Storm discharge at pumping station |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | SY4555089120 | GB620806560000 | Lyme Bay East | LYME BAY (C) |  |  |  |  | Commissioned in 2020 - full year data expected | 5 | 9 | 9 | 15 | 58.5 | 99.9971 | 9.5 | 3 (installed 2020) | [5 empty] | 2022-03-17 | No sewage litter or sewage fungus | 2022-03-17 | TRAC site - N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620806560000 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13341S | WESTWOOD STORM TANK | 102716 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | WEST WILTSHIRE | Chippenham Co Const | ST8052858559 | GB109053021840 | Somerset Frome conf with Mells to conf B. Avo | TRIBUTARY OF RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 40 | 20 | 17 | 33 | 483 | 99.9887 | 30.4 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021840 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13345S | WICK MANOR ROAD STORM TANK | 011563 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6926071930 | GB109053027510 | Boyd - source to conf R Avon (Brist) | RIVER BOYD |  |  |  |  | Commissioned in 2018 - full year data expected | 40 | 22 | 20 | 56 | 537.3333 | 99.9951 | 34.2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027510 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13347S | WICKWAR STORM TANK | 010304 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | STROUD | The Cotswolds Co Const | ST7278089501 | GB109054026580 | Little Avon R - source to conf Ozleworth Bk | LITTLE AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 35 | 22 | 19 | 47 | 242.8333 | 100 | 31.2 | 5 (installed 2018) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026580 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13350S | WINCANTON STORM TANK | 401609 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST7106027380 | GB108043015850 | Cale | RIVER CALE(S) |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 39 | 70 | 906.6 | 99.9292 | 54.5 | 2 (installed 2021) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2023-09-27 | No sewage litter or sewage fungus | 2023-09-27 | TBC |  |  | 2018-06-08 | Field based assessment - No impact | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015850 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13354S | WIVELISCOMBE HILLSMOOR STORM TANK | NPSWQD000307 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST0861827364 | GB108052015510 | Hillfarrance Bk | TRIB OF HILLFARRANCE BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 28 | 28 | 19 | 38 | 173 | 99.9092 | 28.25 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015510 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13360S | ROYAL WOOTTON BASSETT STORM TANK | 100673 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | SU0740681472 | GB109053027740 | Brinkworth Brook | HANCOCK'S WATER |  |  |  |  | Commissioned in 2017 - full year data expected | 31 | 16 | 20 | 56 | 665.1333 | 99.9996 | 30.6667 | 6 (installed 2017) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2021-09-21 | No sewage litter or sewage fungus | 2021-09-21 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027740 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13522S | LYNEHAM B SITE (MAIN STW) RAF LYNEHAM STORM TANK | 100854 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | NORTH WILTSHIRE | North Wiltshire Co Const | SU0272477764 | GB109053027640 | Cowage Bk - source to conf unnamed trib | SPRINGS WATERCOURSE |  |  |  |  | Commissioned in 2019 - full year data expected | 34 | 12 | 26 | 60 | 1060.75 | 99.9886 | 31.2 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027640 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13966C | LITTLETON PANELL CORNBURY MILL | Unpermitted | SO on sewer network |  | Diluted | Rainwater | KENNET | Devizes Co Const | SU0059453907 | GB109053022130 | Semington Bk - source to conf Worton Str | Semington Bk - source to conf Worton Str |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 22 | 27 | 29.9333 | 99.4053 | 24.5 | 1 (installed 2022) | [5 empty] | 2022-09-30 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022130 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14059B | ROWDE TOWER VIEW | 103621 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | KENNET | Devizes Co Const | ST9753862920 | GB109053022220 | Summerham Brook | TRIBUTARY OF SUMMERHAM BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 35 | 34 | 24 | 41 | 113.75 | 99.5481 | 29.6667 | 6 (installed 2017) | [9 empty] | 2021-11-16 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022220 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14082B | STREET MAIN | 100740 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Wells Co Const | ST4809837275 | GB108052021181 | South Drain | TRIB OF SOUTH DRAIN |  |  |  |  | Commissioned in 2018 - full year data expected | 32 | 40 | 29 | 43 | 171.75 | 99.9635 | 35 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021181 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14083B | WEST PENNARD HAVYATT | 102369 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | MENDIP | Somerton and Frome Co Const | ST5389038120 | GB108052021171 | Hartlake | TRIB OF RIVER BRUE(S) |  |  |  |  | Commissioned in 2019 - full year data expected | 35 | 26 | 22 | 56 | 544.1167 | 99.8019 | 34.75 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021171 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14095B | GLASTONBURY PORCHESTALL | 071825 | Storm discharge at pumping station |  | Diluted | Rainwater | MENDIP | Wells Co Const | ST4912038850 | GB108052021190 | Brue - Clyce Hole to conf North Drain | RIVER BRUE MILL STREAM (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 46 | 35 | 18 | 46 | 246.8 | 99.8699 | 34 | 5 (installed 2018) | [9 empty] | 2022-05-05 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021190 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14102B | KILMERSDON | 102698 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Somerton and Frome Co Const | ST6968152558 | GB109053022230 | Kilmersdon Str - source to conf Snails Bk | KILMERSDON STREAM |  |  |  |  | Commissioned in 2019 - full year data expected | 59 | 43 | 44 | 39 | 165.5412 | 100 | 37 | 4 (installed 2019) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022230 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14126B | SHROTON | 402122 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | NORTH DORSET | North Dorset Co Const | ST8611612337 | GB108043016010 | Iwerne | RIVER IWERNE |  |  |  |  | Commissioned in 2018 - full year data expected | 21 | 0 | 1 | 17 | 226.25 | 99.9345 | 8.6 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016010 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14235B | BOVINGTON DUNCAN CRESCENT | 401420 | Storm discharge at pumping station |  | Diluted | Rainwater | PURBECK | South Dorset Co Const | SY8397488935 | GB108044009692 | Frome Dorset (Lower) d/s Louds Mill Dorchester | TRIBUTARY OF THE RIVER FROME |  |  |  |  | Commissioned in 2020 - full year data expected |  | 7 | 7 | 15 | 23.9667 | 100 | 9.6667 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009692 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14263B | CORFE CASTLE RED LANE | 401200 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SY9647081690 | GB108044010020 | Corfe River | TRIB OF CORFE RIVER (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 13 | 4 | 5 | 14 | 42.2439 | 99.9829 | 8.4 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010020 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14285B | MISTERTON | 103598 | Storm discharge at pumping station |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST4617008560 | GB108052015260 | Parrett - headwaters to Broad River | TRIB OF RIVER PARRETT |  |  |  |  | Commissioned in 2020 - full year data expected |  | 26 | 21 | 31 | 132.8886 | 99.9416 | 26 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015260 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14287B | HINTON ST GEORGE | 102398 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST4226012250 | GB108052015290 | Merriot Stream | MERRIOTT STREAM(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 30 | 36 | 29 | 40 | 236.8 | 96.4372 | 33.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015290 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14301B | STALBRIDGE | 050979 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH DORSET | North Dorset Co Const | ST7469017394 | GB108043016060 | Stour Trib (Bibbern Brook) | BIBBERN BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 42 | 27 | 33 | 66 | 519.9167 | 100 | 39.4 | 5 (installed 2018) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016060 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14394B | WELLINGTON MITCHELLS POOL | 100238 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST1454720895 | GB108052015390 | Haywards Water | HAYWARDS WATER |  |  |  |  | Commissioned in 2017 - full year data expected | 43 | 21 | 20 | 33 | 201.75 | 99.8781 | 25.5714 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015390 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14402B | OSMINGTON PONTINS | 051316 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST DORSET | South Dorset Co Const | SY7202082030 | GB620705550000 | Dorset / Hampshire | ENGLISH CHANNEL |  |  |  |  | Commissioned in 2020 - full year data expected |  | 14 | 3 | 17 | 39.9 | 99.9499 | 11.3333 | 3 (installed 2020) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | 2023-10-04 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620705550000 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14425B | CLUTTON GREENBROOK | 102915 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6267058980 | GB109053022290 | Cam Bk - source to conf Wellow Bk | TRIB OF CAM BROOK |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 31 | 39 | 204.1833 | 98.289 | 35 | 2 (installed 2021) | [9 empty] | 2021-12-13 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022290 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14430B | CHEW MAGNA DUMPERS LANE | 102223 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST5782062900 | GB109053021852 | Chew - Chew Valley Lake to conf Winford Brook | RIVER CHEW(S) |  |  |  |  | Commissioned in 2020 - full year data expected | 76 | 31 | 7 | 38 | 197.3556 | 100 | 38 | 3 (installed 2020) | [9 empty] | 2021-12-09 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021852 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14531S | MIDFORD TUCKING MILL | 021434 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST7600060000 | GB109053022271 | Wellow Bk - Snails Bk to Bristol Avon | TRIB OF MIDFORD BROOK (S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 13 | 30 | 123.2694 | 99.9993 | 21.5 | 1 (installed 2022) | [9 empty] | 2023-01-03 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022271 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15071B | ST LEONARDS CRAIGSIDE ROAD | 401243 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | EAST DORSET | Christchurch Co Const | SU1063703483 | GB108043016090 | Crane (Dorset) | TRIB OF MOORS RIVER |  |  |  |  | Commissioned in 2019 - full year data expected | 4 | 5 | 1 | 6 | 28.9635 | 96.7953 | 5.8 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016090 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15073B | WIMBORNE PILFORD HEATH | 042514 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | EAST DORSET | Mid Dorset and North Poole Co Const | SU0348001670 | GB108043011080 | Uddens Water | TRIB OF UDDENS WATER (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 31 | 24 | 22 | 27 | 58.9 | 99.664 | 26 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011080 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15082B | WIMBORNE BROOK ROAD NO 1 | 401779 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | EAST DORSET | Mid Dorset and North Poole Co Const | SZ0232699908 | GB108043011040 | Stour (Lower) | TRIBUTARY OF THE RIVER STOUR |  |  |  |  | Commissioned in 2018 - full year data expected | 3 | 4 | 0 | 3 | 3.75 | 99.999 | 2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011040 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15106B | POULSHOT TOWNSEND | 102478 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | KENNET | Devizes Co Const | ST9609058770 | GB109053022190 | Poulshot Str - source to conf Summerham Bk | TRIB OF SUMMERHAM BROOK(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 19 | 14 | 28 | 39 | 521.4167 | 99.98 | 25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022190 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15166B | RANGEWORTHY BERROWS MEAD | 103233 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6948086190 | GB109053027590 | Laddon Bk - source to conf R Frome (Brist) | TRIBUTARY OF LADDEN BROOK(S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 21 | 104 | 2079.3667 | 99.9855 | 62.5 | 1 (installed 2022) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue |  |  |  |  | 2021-12-16 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027590 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15200B | MARNHULL SODOM LANE | 402474 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH DORSET | North Dorset Co Const | ST7886019380 | GB108043016051 | Stour (Middle u/s Pimperne Brook) | THE CHIVRICKS BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 35 | 18 | 35 | 50 | 403.75 | 99.9558 | 34.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016051 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15201B | DURWESTON WATER LANE | 402475 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | NORTH DORSET | North Dorset Co Const | ST8602308806 | GB108043016051 | Stour (Middle u/s Pimperne Brook) | TRIBUTARY OF RIVER STOUR |  |  |  |  | Commissioned in 2018 - full year data expected | 18 | 24 | 51 | 72 | 558.9333 | 99.9996 | 29.6667 | 5 (installed 2018) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016051 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15243B | BRIDGWATER EAST QUAY | 071343 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3005037340 | 200 | Not part of a river WB catchment | RIVER PARRETT (E) |  | BURNHAM JETTY NORTH | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=burnh&site=ukk2302-35300 |  | Commissioned in 2016 - full year data expected | 46 | 29 | 26 | 39 | 36.5008 | 100 | 34.375 | 7 (installed 2016) | [13 empty] | Not part of a river WB catchment | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15253B | POOLE FAIRVIEW ROAD | 401394 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | POOLE | Mid Dorset and North Poole Co Const | SZ0050096390 | GB108043011040 | Stour (Lower) | TRIB OF RIVER STOUR(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 7 | 5 | 5 | 7 | 19.3667 | 99.4859 | 6 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011040 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15277B | POOLE WOOD LANE | 401257 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | POOLE | Mid Dorset and North Poole Co Const | SZ0546096960 | GB108043011040 | Stour (Lower) | FRESHWATER(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 24 | 18 | 25 | 24 | 110.3333 | 99.9191 | 22.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011040 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15290B | HENSTRIDGE MARSH LANE (HENSTRIDGE NO 2) | 050882 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST7325020140 | GB108043015822 | Henstridge Stream | TRIBUTARY OF RIVER CALE |  |  |  |  | Commissioned in 2019 - full year data expected | 19 | 22 | 26 | 37 | 287.4833 | 99.9994 | 23.6667 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015822 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15304B | WEST CHINNOCK GARAGE | 103720 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST4692013840 | GB108052015310 | Chinnock BK | THE CHINNOCK BROOK(S) |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 20 | 23 | 108.9876 | 99.9753 | 21.5 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015310 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15317B | NORTON SUB HAMDON | 103178 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST4681215495 | GB108052015360 | Parrett - Lopen Bk to R Isle | TRIBUTARY OF RIVER PARRETT |  |  |  |  | Commissioned in 2018 - full year data expected | 57 | 31 | 28 | 53 | 546.1333 | 99.945 | 37.1667 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015360 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15327B | ILMINSTER LORD NELSON | 102397 | Storm discharge at pumping station |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST3485215060 | GB108052015190 | Isle - Upper to conf Cad Bk | FRESHWATER (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 10 | 6 | 1 | 9 | 65.7333 | 99.2211 | 6.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015190 | Yes |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15331B | SHEPTON BEAUCHAMP | 102005 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST4074017120 | GB108052015340 | Lam Brook | LAMBROOK BROOK(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 27 | 27 | 30 | 50 | 313.1667 | 98.2806 | 33.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015340 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15388B | OTHERY RYE LANE/ SUMMERHEDGE ROAD | 101715 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3849031360 | GB108052021150 | King's Sedgemoor Drain - Henley Sluice to mouth | TRIB OF SOWY RIVER (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 6 | 7 | 7 | 9 | 57.7 | 99.6123 | 7.25 | 5 (installed 2018) | [9 empty] | 2022-03-01 | Inaccessible at time of visit |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021150 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15414B | BRISTOL CENTRAL TRADING ESTATE BATH ROAD | 021635 | Storm discharge at pumping station |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6075371860 | 157 | Not part of a river WB catchment | RIVER AVON (ESTUARINE) |  |  |  |  | Commissioned in 2019 - full year data expected | 5 | 10 | 4 | 4 | 4.8333 | 99.8516 | 5.75 | 4 (installed 2019) | [13 empty] | Not part of a river WB catchment | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15461B | STOKE ST GREGORY WOODHILL | 103188 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST3531527010 | GB108052015450 | West Sedgemoor Main Drain | TRIB OF WEST SEDGEMOOR M DRAIN |  |  |  |  | Commissioned in 2019 - full year data expected | 5 | 9 | 3 | 6 | 52.4167 | 99.9871 | 5.75 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015450 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15463B | BRADFORD ON TONE TONE GREEN | 103189 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | TAUNTON DEANE | Taunton Deane Co Const | ST1719023006 | GB108052015481 | Tone - Wellington to Taunton | RIVER TONE |  |  |  |  | Commissioned in 2019 - full year data expected | 7 | 9 | 6 | 18 | 283.5 | 91.6929 | 10 | 4 (installed 2019) | [5 empty] | 2023-10-04 | No sewage litter or sewage fungus | 2023-10-04 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015481 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15469B | LEIGH FRAMPTON FARM | 102977 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | ST6133808503 | GB108052015540 | Wriggle River | TRIBUTARY OF WRIGGLE RIVER |  |  |  |  | Commissioned in 2019 - full year data expected | 37 | 20 | 30 | 49 | 199.718 | 100 | 33.4 | 4 (installed 2019) | [9 empty] | 2022-02-16 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015540 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15494B | ABBOTSBURY CHURCH STREET | 401866 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | SY5771085025 | 2 | Not part of a river WB catchment | MILL STREAM |  |  |  |  | Commissioned in 2019 - full year data expected | 8 | 5 | 8 | 17 | 25.6667 | 100 | 9.8 | 4 (installed 2019) | [9 empty] | 2021-11-17 | Baseline data, SO not discharging when sampled |  |  | Not part of a river WB catchment | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15495B | NETHERBURY BEAMINSTER | 402106 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | SY4721899206 | GB108044009600 | Brit (Upper) | RIVER BRIT |  |  |  |  | Commissioned in 2020 - full year data expected |  | 33 | 39 | 82 | 1076.1333 | 99.9271 | 51.3333 | 3 (installed 2020) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009600 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15508B | WOOTTON COURTENAY | 102300 | Storm discharge at pumping station |  | Diluted | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | SS9335043450 | GB108051020230 | Aller | RIVER AVILL (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 7 | 6 | 4 | 6 | 8.25 | 96.9121 | 5.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108051020230 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15544C | TEMPLE CLOUD BRIDGE | 021357 | Storm discharge at pumping station |  | Diluted | A combination of rainwater and groundwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6255857351 | GB109053022290 | Cam Bk - source to conf Wellow Bk | CAM BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 41 | 38 | 42 | 55 | 426.2308 | 99.9529 | 34.5714 | 6 (installed 2017) |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | [5 empty] | 2021-12-13 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022290 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15627B | ILTON FROST LANE | 070693 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST3557017330 | GB108052015180 | Ding | CAD BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 41 | 31 | 12 | 19 | 203.5 | 99.9917 | 27.5 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015180 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15630B | CHICKERELL LOWER WAY | EPRCB3990NR | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | SY6491080495 | GB108044010210 | Wey | TRIB OF THE RIVER WEY | PORTLAND NORTH EASTERN BREAKWATER |  |  |  | Commissioned in 2016 - full year data expected | 7 | 9 | 3 | 4 | 6.9333 | 100 | 4 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010210 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15651C | BRIDPORT SOUTH BRIDGE TANK | 400444 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | SY4660092240 | GB108044009580 | Asker | RIVER ASKER(S) |  |  |  |  | Commissioned in 2016 - full year data expected | 33 | 35 | 26 | 41 | 236.5167 | 99.9884 | 31.5 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009580 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16011C | BATH ENGLISHCOMBE LANE / STIRTINGDALE ROAD JUNCTION | 102605 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7343164926 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 12 | 11 | 3 | 4 | 0.3 | 94.8893 | 7.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16045C | BATH ST JOHNS RC PRIM SCHOOL AT REAR NR RECREATION GROUND | 102777 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7538064720 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 29 | 27 | 16 | 26 | 23.25 | 88.8927 | 24.5 | 5 (installed 2018) | Telemetry or data archiving failure / issue | Resolved - Feb | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16050C | BATH EA DEPOT | 102275 | SO on sewer network |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7240064870 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 7 | 5 | 3 | 6 | 22.25 | 100 | 5.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16067C | BATH LADYMEAD HOUSE (R/O) WALCOT | 103043 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7517165389 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 39 | 31 | 28 | 45 | 71.7 | 99.6758 | 26.875 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16081C | BATH ROCKCLIFFE ROAD R/O NO 45 | 010853 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7554865762 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 34 | 26 | 17 | 23 | 21.9667 | 85.4985 | 18.875 | 5 (installed 2018) | Sensor failure / issue | Resolved - Feb | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16083C | BATH KENSINGTON MEADOWS BUS DEPOT STORM TANK | 100677 | SO on sewer network |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7568065810 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2016 - full year data expected | 49 | 20 | 29 | 63 | 522 | 99.9924 | 39.125 | 7 (installed 2016) |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | 2021-03-29 | Sewage litter present, no sewage fungus |  | N/A | 2022-03-01 | Water Quality Modelling shows that the WFD Status Class at the 99%ile level for BOD and Ammonia is High ‘with’ or ‘without’ all Bath FSOs |  | Multiple overflows so unsuitable for invertebrate assessment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16099C | BATH PRIOR PARK ROAD OPP NO 9 | NPSWQD002500 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7538564298 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 6 | 8 | 3 | 5 | 1.0667 | 99.8398 | 5.4 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16138C | BRISTOL QUEEN STREET / MEADOW STREET | 102069 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5168378645 | GB109054026650 | Chestle Pill | RIVER SEVERN VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 9 | 12 | 5 | 12 | 22.4497 | 98.8449 | 15.1667 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026650 | No |  |  | 2045 | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16161C | BRISTOL CENTRAL INDUSTRIAL ESTATE BATH ROAD | 100590/CS/01 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6044071704 | GB530905415405 | BRISTOL AVON | RIVER AVON (ESTUARINE) |  |  |  |  | Commissioned in 2018 - full year data expected | 1 | 9 | 6 | 5 | 1.1 | 99.6545 | 5.2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16168C | BRISTOL PETHERTON ROAD PAINT FACTORY | 100574 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST6031069780 | GB109053021980 | Brislington Bk - source to conf R Avon (Brist) | BRISLINGTON BROOK, VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 5 | 36 | 80.5667 | 99.6697 | 20.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021980 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16190C | BRISTOL CATTLE MARKET ROAD SIPHON | 102829 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5991872268 | GB530905415405 | BRISTOL AVON | RIVER AVON (ESTUARINE) |  |  |  |  | Commissioned in 2017 - full year data expected | 5 | 8 | 7 | 16 | 31.9167 | 99.9875 | 8.7143 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16252C | BRISTOL ROSE GREEN ROAD | 102145 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6177074840 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | COOMBE BROOK VIA SWS |  |  |  |  | Commissioned in 2017 - full year data expected | 70 | 26 | 19 | 31 | 9.9167 | 99.968 | 38.4286 | 6 (installed 2017) | [5 empty] | 2020-11-30 | No sewage litter or sewage fungus | 2020-11-30 | Lab assessment - No impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16254C | BRISTOL STAPLETON ROAD / GLENFROME ROAD | 101747 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6115175638 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 15 | 42 | 28 | 50 | 29.9667 | 99.5841 | 29 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16292C | BRISTOL BISHOP ROAD / 214 GLOUCESTER ROAD | 013056 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5612074460 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2017 - full year data expected | 4 | 11 | 5 | 8 | 1.0333 | 99.4741 | 6 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16322C | BRISTOL HIGH STREET / ST MARKS ROAD | 103310 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST6042774443 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME |  |  |  |  | Jan 2023 |  |  |  | 0 | 0 | 99.6189 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16330C | BRISTOL MEADOW VALE NO 40 FRONT GARDEN | 103313 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST5612074460 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2018 - full year data expected | 6 | 8 | 3 | 3 | 0.23333 | 99.8874 | 5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16341C | BRISTOL SPEEDWELL ROAD / VENTNOR ROAD | 101797 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST5611874456 | GB530905415405 | BRISTOL AVON | RIVER AVON (E) VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 7 | 10 | 3 | 2 | 0.066667 | 99.7546 | 5.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16348C | BRISTOL ASHLEY DOWN ROAD ALLOTMENTS | EPRAP3921GT | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5611874456 | GB530905415405 | BRISTOL AVON | THE RIVER AVON (E) VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 6 | 13 | 5 | 4 | 2.0667 | 99.7549 | 7 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16374C | BRISTOL HARBURY ROAD / WELLINGTON HILL W | 100471 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5815577315 | GB109053027530 | Trym - source to conf R Avon (Brist) | TRIB OF RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 13 | 5 | 1 | 1 | 0.066667 | 99.8154 | 5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16382C | BRISTOL LAWRENCE GROVE O/S NO 21 | 100476 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5801877358 | GB109053027530 | Trym - source to conf R Avon (Brist) | TRIB OF RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected |  | 6 | 6 | 0 | 0 | 99.922 | 4 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16406C | BRISTOL WELLINGTON HILL WEST NO 175 | 100472 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5815577315 | GB109053027530 | Trym - source to conf R Avon (Brist) | RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected |  | 10 | 7 | 8 | 5.2 | 99.9737 | 8.3333 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16415C | BRISTOL PRINCE STREET ROUNDABOUT | 100456 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5856772056 | 157 | Not part of a river WB catchment | TRIBUTARY OF THE RIVER AVON |  |  |  |  | Commissioned in 2019 - full year data expected | 8 | 8 | 5 | 17 | 57.8667 | 99.75 | 9.5 | 4 (installed 2019) | [13 empty] | Not part of a river WB catchment | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16417C | BRISTOL AVON STREET / OXFORD STREET | 101095 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5986872604 | GB530905415405 | BRISTOL AVON | FLOATING HARBOUR |  |  |  |  | Commissioned in 2018 - full year data expected | 11 | 13 | 12 | 12 | 8.4333 | 99.6431 | 9.7143 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2045 | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16472C | BRISTOL KINGSWOOD WOOD ROAD | 101751 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6403073340 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | STRAD BROOK VIA SWS |  |  |  |  | Commissioned in 2017 - full year data expected | 29 | 26 | 13 | 40 | 18.5667 | 87.883 | 27.5 | 6 (installed 2017) | Sensor failure / issue | Resolved - Jul |  |  |  | 2020-11-03 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16479C | BRISTOL KINGSWOOD NEW CHELTENHAM ROAD NO 20 | 100893 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6631974374 | GB109053027450 | Siston Bk - source to conf R Avon (Brist) | WARMLEY BROOK |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 23 | 73 | 68.2333 | 97.6412 | 48 | 2 (installed 2021) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027450 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16487C | BRISTOL KINGSWOOD STATION ROAD OPP 61 | 100929 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6625874582 | GB109053027450 | Siston Bk - source to conf R Avon (Brist) | WARMLEY BROOK (S) |  |  |  |  | Apr 2023 |  |  |  | 1 | 0.16667 | 99.7451 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027450 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16501C | FROME FARRANT ROAD NEAR YOUTH CENTRE | 100438 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Somerton and Frome Co Const | ST7714448726 | GB109053022101 | Frome (Maiden Bradley to Mells) | RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 35 | 31 | 34 | 47 | 18.7 | 99.9258 | 29 | 5 (installed 2018) | [5 empty] | 2023-11-16 | No sewage litter or sewage fungus | 2023-03-02 | N/A |  |  |  | Unsafe for lone working | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022101 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16506C | FROME WHATCOMBE ROAD NO 20 | 100441 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Somerton and Frome Co Const | ST7732348617 | GB109053022101 | Frome (Maiden Bradley to Mells) | RIVER FROME VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 43 | 35 | 34 | 42 | 17.7 | 91.8527 | 32.1429 | 5 (installed 2018) | [5 empty] | 2023-11-16 | Sewage litter present, no sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022101 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16508C | FROME COURT HOUSE KING STREET | 100443 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Somerton and Frome Co Const | ST7784448085 | GB109053022101 | Frome (Maiden Bradley to Mells) | RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 38 | 20 | 23 | 29 | 8.7333 | 99.8721 | 22.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022101 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16551C | SHAFTESBURY HOLLYROOD FARM | 401301 | SO on sewer network |  | Diluted | Rainwater | NORTH DORSET | North Dorset Co Const | ST8613622028 | GB108043016110 | Stirchell Brook | TRIB OF STIRCHELL BROOK |  |  |  |  | Commissioned in 2020 - full year data expected | 25 | 20 | 26 | 23 | 8.7667 | 89.7641 | 23.5 | 3 (installed 2020) | Telemetry or data archiving failure / issue | Resolved - Aug | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016110 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16558C | FRAMPTON COTTERELL RECTORY ROAD O/S 54 PARSONAGE BRIDGE (NW) | 103073 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6653681713 | GB109053027820 | Frome (Brist) - conf Laddon Bk to conf Folly Bk | RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 44 | 32 | 15 | 43 | 226.7667 | 99.8965 | 38.7143 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027820 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16574C | MALMESBURY DARK LANE / 8 FOXLEY LANE | 012852 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9285287256 | GB109053027690 | Sherston Avon | SHERSTON AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 35 | 31 | 33 | 55 | 24.4333 | 99.9513 | 31.3333 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027690 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16585C | CALNE MARDEN HOUSE CULVERT AT REAR | 100775 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9971470764 | GB109053022050 | Marden - source to conf Cowage Bk | RIVER MARDEN |  |  |  |  | Commissioned in 2018 - full year data expected | 30 | 18 | 16 | 25 | 76.9667 | 94.2169 | 22 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022050 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16596C | CALNE QUEMERFORD BRIDGE | 102552 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | SU0065569807 | GB109053022050 | Marden - source to conf Cowage Bk | RIVER MARDEN |  |  |  |  | Commissioned in 2018 - full year data expected | 49 | 24 | 24 | 46 | 262.6333 | 99.5875 | 35.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022050 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16604C | SHERSTON THE TARTARS | 102886 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST8562885726 | GB109053027690 | Sherston Avon | RIVER AVON (SHERSTON BRANCH) |  |  |  |  | Commissioned in 2018 - full year data expected | 35 | 29 | 25 | 41 | 14.7667 | 99.7393 | 29.3333 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027690 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16609C | CALNE MOSSES MILL 1 | 100772 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9877070738 | GB109053022050 | Marden - source to conf Cowage Bk | RIVER MARDEN |  |  |  |  | Feb 2023 |  |  |  | 0 | 0 | 99.6739 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022050 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16632C | WAREHAM ABBOTTS QUAY | 051049 | SO on sewer network |  | Diluted | Rainwater | PURBECK | Mid Dorset and North Poole Co Const | SY9229887168 | GB520804415800 | POOLE HARBOUR | RIVER FROME (ESTUARINE) |  |  |  |  | Commissioned in 2017 - full year data expected | 6 | 3 | 3 | 9 | 8.75 | 100 | 7.5714 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB520804415800 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16657C | MAIDEN BRADLEY STW ADJ TO | 041306 | SO on sewer network |  | Diluted | Rainwater | SALISBURY | South West Wiltshire Co Const | ST8071538587 | GB108043022520 | Wylye (Headwaters) | TRIBUTARY OF RIVER WYLYE |  |  |  |  | Commissioned in 2019 - full year data expected | 3 | 10 | 12 | 6 | 1.0333 | 63.8558 | 7.75 | 4 (installed 2019) | Sensor failure / issue | Scheduled |  |  |  | 2018-11-16 | Sewage litter present, no sewage fungus | [6 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022520 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16684C | YEOVIL COOPERS MILL HENDFORD | 101783 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5534115460 | GB108052015600 | Dodham Brook (Yeo (Somset)) | DODHAM BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 24 | 21 | 19 | 32 | 24.5 | 100 | 30.4286 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015600 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16685C | YEOVIL GOLDCROFT | 071700 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5639515975 | GB108052015600 | Dodham Brook (Yeo (Somset)) | DODHAM BROOK VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 28 | 54 | 16.6667 | 94.2607 | 41 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015600 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16691C | YEOVIL HORSEY LANE | 101784 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5520815508 | GB108052015600 | Dodham Brook (Yeo (Somset)) | DODHAM BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 21 | 17 | 18 | 23 | 31.9167 | 100 | 21.4 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015600 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16705C | NORTH PERROTT OLD STW SITE | 102403 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST4764810196 | GB108052015270 | Broad | TRIB OF SMALL BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 70 | 36 | 8 | 49 | 177.3333 | 99.9962 | 37.5714 | 6 (installed 2017) |  |  | Performance - Other maintenance / capital works (e.g. jetting) | Resolved - Mar | N/A - Operational solution applied | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015270 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16710C | STOKE SUB HAMDON QUEENS CRESCENT R/O (OS 5300) | 100695 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST4764618197 | GB108052015350 | Wellhams Brook | TRIBUTARY OF WELLHAMS BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 43 | 33 | 32 | 44 | 47.7667 | 89.8033 | 38 | 4 (installed 2019) | Telemetry or data archiving failure / issue | Resolved - Aug | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015350 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16716C | WINCANTON BENNET FIELD | 402524 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST7108627887 | GB108043015850 | Cale | RIVER CALE |  |  |  |  | Commissioned in 2017 - full year data expected | 31 | 20 | 17 | 29 | 40.3333 | 100 | 27 | 6 (installed 2017) | [5 empty] | 2023-09-27 | No sewage litter or sewage fungus | 2023-09-27 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015850 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16731C | TAUNTON GOOSENFORD | 102261 | SO on sewer network |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST2495627755 | GB108052015460 | Allen Brook(Maiden brook) | ALLEN'S BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 28 | 17 | 213.2 | 82.2036 | 22.5 | 1 (installed 2022) | Sensor failure / issue | Resolved - Dec | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015460 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16744C | CHEDDON FITZPAINE MAIDENBROOK LANE | 102262 | SO on sewer network |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST2436027410 | GB108052015460 | Allen Brook(Maiden brook) | TRIB OF OLD RIVER TONE |  |  |  |  | Commissioned in 2018 - full year data expected |  | 40 | 33 | 64 | 541.4 | 96.667 | 37.6 | 5 (installed 2018) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2021-05-17 | No sewage litter or sewage fungus | 2021-05-17 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015460 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16755C | BATHAMPTON M H K | 100510/CS/01 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST7723366713 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2019 - full year data expected | 30 | 21 | 13 | 26 | 7.2 | 99.8166 | 22.5 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16758C | BATHAMPTON MILL LANE | 100511/CS/01 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST7740966882 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 46 | 28 | 25 | 39 | 205.6667 | 99.8729 | 34.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16763C | KEYNSHAM ST LADOC / BRISTOL ROAD | 102128 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6477069000 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | CHARLTON BOTTOM VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 23 | 29 | 18 | 33 | 7.8667 | 99.9823 | 23.4286 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16769C | RADSTOCK KILMERSDON ROAD SYPHON EO | 013130 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6892554592 | GB109053022240 | Snails Bk - source to conf Kilmersdon Str | WATERSIDE |  |  |  |  | Commissioned in 2018 - full year data expected | 33 | 20 | 19 | 42 | 33.4 | 99.9041 | 28.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022240 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16773C | MIDSOMER NORTON WELTON SO | 021351 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6650054800 | GB109053022250 | Wellow Bk - source to conf Snails Bk | TRIB OF MIDFORD BROOK (S) |  |  |  |  | Commissioned in 2019 - full year data expected | 7 | 9 | 6 | 6 | 0.76667 | 92.003 | 7 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022250 | Yes |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16789C | MONKTON COMBE SUMMER LANE | 100509/CS/01 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7635261625 | GB109053022271 | Wellow Bk - Snails Bk to Bristol Avon | HORSECOMBE BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 31 | 36 | 25 | 31 | 13.9167 | 99.9876 | 32.1429 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022271 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16818C | BROADMAYNE KNIGHTON LANE (PUMPED) | 401593 | SO on sewer network |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | SY7308086600 | GB108044009660 | Tadnoll Brook (including Empool Bottom) | TADNOLL BROOK(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 82 | 37 | 24 | 30 | 111.2931 | 99.9863 | 43.25 | 5 (installed 2018) |  |  | Performance - Infiltration | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009660 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14268B | WAREHAM NORTH BRIDGE | Unpermitted | Storm discharge at pumping station |  | Diluted | Rainwater | PURBECK | Mid Dorset and North Poole Co Const | SY9215387815 | GB520804415800 | POOLE HARBOUR | POOLE HARBOUR |  |  |  |  | Oct 2023 |  |  |  | 16 | 149.3333 | 97.6351 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010080 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16900C | TROWBRIDGE CANAL ROAD | 102027 | SO on sewer network |  | Diluted | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8533859047 | GB109053021791 | Biss (Bitham Bk to Bristol Avon) | RIVER BISS VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 46 | 21 | 21 | 32 | 159.6 | 99.812 | 30.8 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021791 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16999C | CREWKERNE NORTH OLD STW SITE | 072347 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST4407510993 | GB108052015290 | Merriot Stream | GOULDS BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 31 | 13 | 17 | 14 | 38.3333 | 99.7184 | 18.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015290 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17224C | BRISTOL IRVING CLOSE SEYMOUR ROAD | 103074 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Filton and Bradley Stoke Co Const | ST6610075400 | GB109053027450 | Siston Bk - source to conf R Avon (Brist) | TRIB OF WARMLEY BROOK VIA SWS |  |  |  |  | Commissioned in 2017 - full year data expected | 31 | 38 | 32 | 59 | 46.9167 | 99.9876 | 27 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027450 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17329C | BRISTOL OPPOSITE 83 AIRPORT ROAD | 103287 | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol South Boro Const | ST6059069890 | GB109053021980 | Brislington Bk - source to conf R Avon (Brist) | BRISLINGTON BROOK(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 43 | 37 | 33 | 59 | 241.6667 | 99.999 | 43 | 5 (installed 2018) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021980 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17338C | TAUNTON MARKET | EPRJB3796RN | SO on sewer network |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST2307525314 | GB108052015482 | Tone Ds Taunton | RIVER TONE |  |  |  |  | Commissioned in 2018 - full year data expected | 2 | 8 | 8 | 22 | 175.4 | 99.7291 | 9 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015482 | Yes |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17384C | BRISTOL DEVONSHIRE ROAD O/S 75 | NPSWQD010514 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5861075072 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | CRANBROOK VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected |  | 31 | 24 | 32 | 5.4667 | 99.9959 | 29 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17450C | BRISTOL ELLESMERE ROAD R/O 15 AND 16 | 103766 | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol East Boro Const | ST6158669928 | GB109053021980 | Brislington Bk - source to conf R Avon (Brist) | TRIB OF THE BRISLINGTON BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 39 | 58 | 316.4667 | 94.6663 | 48.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021980 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17502C | BRISTOL CRANBROOK ROAD O/S NO 192 | 011793 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5861075072 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | CRANBROOK BROOK VIA SWS |  |  |  |  | Commissioned in 2021 - full year data expected |  | 22 | 20 | 27 | 4.5 | 98.726 | 23 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17541C | BATH LARKHALL TERRACE FIELD TO REAR | 103902 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7624766576 | GB109053022300 | Lam Bk - source to conf R Avon (Brist) | LAM BROOK VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 38 | 31 | 26 | 35 | 24.4667 | 99.7549 | 30.1667 | 5 (installed 2018) | [5 empty] | 2018-02-05 | No sewage litter or sewage fungus | [5 empty] | No sewage fungus assessment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022300 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17892C | TIMSBURY RADFORD HILL | 013267 | SO on sewer network |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6704958482 | GB109053022290 | Cam Bk - source to conf Wellow Bk | TRIB OF CAM BROOK (S) |  |  |  |  | Commissioned in 2016 - full year data expected |  | 34 | 27 | 52 | 132.0844 | 100 | 37.6667 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022290 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19035B | KINGSBURY EPISCOPI | 013464 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST4305021150 | GB108052015230 | Westmoor Main Drain | TRIBUTARY OF RIVER PARRETT (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 10 | 13 | 5 | 16 | 185.75 | 100 | 11 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015230 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19122C | PORTISHEAD COOMBE/SLADE ROAD JUNCTION | 100557/CS/01 | SO on sewer network |  | Diluted | Rainwater | NORTH SOMERSET | North Somerset Co Const | ST4701076250 | GB109052027330 | Portbury Ditch - source to conf R Severn Estuary | TRIBUTARY OF PORTBURY DITCH |  |  |  |  | Commissioned in 2018 - full year data expected | 38 | 21 | 18 | 32 | 17.2 | 99.9696 | 27.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052027330 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19151C | WEYMOUTH CHICKERELL/CHAFFEYS ATTENUATION TANK RADIPOLE | 043152 | SO on sewer network |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6603080050 | GB108044010210 | Wey | TRIBUTARY OF THE RIVER WEY |  |  |  |  | Commissioned in 2018 - full year data expected | 9 | 7 | 10 | 12 | 29.9167 | 99.8392 | 8.3333 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010210 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19156S | CHARD PEASMARSH STORM TANK | 101327 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST3408011800 | GB108052015160 | Isle - Upper | RIVER ISLE |  |  |  |  | Commissioned in 2020 - full year data expected |  | 53 | 25 | 31 | 235.75 | 99.9971 | 36.3333 | 3 (installed 2020) | [7 empty] | 2020-11-24 | Incomplete |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015160 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19556S | SOUTH WRAXALL HOME FARM LOWER WRAXALL STORM TANK | 102755 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | Chippenham Co Const | ST8362063965 | GB109053021890 | Chalfield Brook - source to conf Avon | CHALFIELD BROOK(S) |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 20 | 32 | 436.8 | 99.9227 | 26 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021890 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19583C | CHILTON POLDEN GOOSE LANE O/S COLLINGS | EPRJB3890RM | SO on sewer network |  | Diluted | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3751440212 | GB108052021181 | South Drain | NIDON BROOK |  |  |  |  | Commissioned in 2020 - full year data expected | 30 | 36 | 42 | 142 | 675.9 | 99.7161 | 62.5 | 3 (installed 2020) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | 2019-03-05 | No sewage litter or sewage fungus | 2019-03-05 | Lab assessment - Impact |  |  |  | RICT analysis complete (Very low) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021181 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15589B | PORTISHEAD POACHER HOTEL (ANCHOR HOTEL) | Unpermitted | Storm discharge at pumping station |  | Diluted | Rainwater | NORTH SOMERSET | North Somerset Co Const | ST4706676149 | GB10905202733 | Portbury Ditch - source to conf R Severn Estuary | Portbury Ditch - source to conf R Severn Estuary |  |  |  |  | Commissioned in 2022 - full year data expected |  |  |  | 10 | 6.3667 | 59.69 | 10 | 1 (installed 2022) | Telemetry or data archiving failure / issue | Resolved - Feb | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052027330 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19777C | BRISTOL FOREST ROAD STORM RETENTION TANK | 101276 | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol East Boro Const | ST6238075802 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | FISHPONDS BROOK VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 25 | 24 | 14 | 33 | 100.5833 | 100 | 24 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19786C | CORSTON MILL LANE | 102555 | SO on sewer network |  | Diluted | A combination of rainwater and groundwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9240784133 | GB109053027730 | Gauze Bk - source to conf R Avon (Brist) | GAUZE BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 32 | 12 | 17 | 57 | 927.9667 | 96.4323 | 26.3333 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027730 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19962C | BRISTOL KINGSWOOD ORCHARD VALE NEW O/S 42 | 101762 | SO on sewer network |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6672572839 | GB109053027450 | Siston Bk - source to conf R Avon (Brist) | SISTON BROOK VIA SWS |  |  |  |  | Commissioned in 2017 - full year data expected | 42 | 34 | 31 | 43 | 35.6667 | 99.999 | 23.7143 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027450 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19975C | FILTON STOKE BROOK | 103135 | SO on sewer network |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Filton and Bradley Stoke Co Const | ST6096080140 | GB109053027540 | Stoke Bk - source to conf Bradley Bk | STOKE BROOK(S) |  |  |  |  | Commissioned in 2020 - full year data expected | 2 | 25 | 34 | 31 | 49.4103 | 100 | 23 | 3 (installed 2020) | [5 empty] | 2018-04-13 | No sewage litter or sewage fungus | 2018-04-13 | Lab assessment - No impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027540 | No |  |  | 2045 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
10375C | SHERBORNE JUNCTION HOUND STREET AND CHEAP STREET | EPRJB3790DC | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | ST6408216250 | GB108052015630 | Yeo | RIVER YEO VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 15 | 20 | 20 | 19 | 5.0667 | 89.011 | 18.5 | 5 (installed 2018) | Telemetry or data archiving failure / issue | Resolved - Mar | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015630 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
10795C | HAMBROOK QUARRY BARTON | 010301 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Filton and Bradley Stoke Co Const | ST6450079500 | GB109053027570 | Bradley Bk - conf Stoke Bk to conf R Brist Frome | BRADLEY BROOK (S) |  |  |  |  | Dec 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [5 empty] | 2022-10-04 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027570 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
10979C | BATH PRIVATE LANE REAR 50 BECKHAMPTON ROAD | 102606 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7391065090 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  |  | 4 | 0.73333 | 99.8786 | 4 | 1 (installed 2022) | [5 empty] | 2022-11-10 | No sewage litter or sewage fungus | 2022-11-10 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
12581C | BRISTOL HULSE ROAD | 011315 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6188170490 | GB109053021980 | Brislington Bk - source to conf R Avon (Brist) | BRISLINGTON BROOK VIA SWS |  |  |  |  | Dec 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021980 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
12938C | BRISTOL O/S 168 STATION ROAD | 010973 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Filton and Bradley Stoke Co Const | ST6103078900 | GB109053027540 | Stoke Bk - source to conf Bradley Bk | SWS-NEW ROAD BROOK-STOKE BROOK |  |  |  |  | Commissioned in 2021 - full year data expected |  |  |  | 25 | 34.2667 | 99.6849 | 25 | 2 (installed 2021) | [5 empty] | 2022-11-16 | No sewage litter or sewage fungus | 2022-11-16 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027540 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13007S | ALVESTON LOWER HAZEL STORM TANK | 010002 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6214087040 | GB109054026650 | Chestle Pill | TOCKINGTON MILL RHINE |  |  |  |  | Commissioned in 2020 - full year data expected |  | 42 | 25 | 67 | 1340.2 | 99.9107 | 44.6667 | 3 (installed 2020) |  |  | Performance - Infiltration | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026650 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13028B | BOWERHILL SHAILS LANE INLET | 102735 | Inlet SO at WwTW |  | Diluted | A combination of rainwater and groundwater | WEST WILTSHIRE | Chippenham Co Const | ST9031162368 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | BERRYFIELD STREAM(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 14 | 7 | 18 | 24 | 115.8 | 99.9951 | 14.4 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13041C | BURTON INLET | 102815 | Inlet SO at WwTW |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST8188079530 | GB109053027500 | By Bk - source to conf Broadmead Bk | BURTON BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 32 | 21 | 22 | 37 | 252.0167 | 99.7835 | 21.8333 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027500 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13051C | CHAFFCOMBE NEAR WAR MEMORIAL INLET | 070015 | Inlet SO at WwTW |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST3521010290 | GB108052015160 | Isle - Upper | TRIB OF RIVER ISLE (S) |  |  |  |  | Jul 2023 |  |  |  | 18 | 10.25 | 99.9987 |  | <1 yr (installed 2023) | [5 empty] | 2023-05-12 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015160 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13072S | COMBE FLOREY STORM TANK | 103010 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST1539031300 | GB108052021390 | Back Stream | TRIBUTARY OF THE BACK STREAM |  |  |  |  | Jul 2023 |  |  |  | 10 | 115.85 | 99.9665 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021390 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13079S | CORSCOMBE OFF FUDGE HILL STORM TANK | 070026 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | ST5208005663 | GB108052015520 | Sutton Bingham Stream - East Arm | HALSTOCK STREAM |  |  |  |  | Commissioned in 2018 - full year data expected | 9 | 17 | 30 | 38 | 196.2 | 99.9014 | 22.4 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015520 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13098B | DOWLISH WAKE KINGSTON INLET | 072317 | Inlet SO at WwTW |  | Diluted | A combination of rainwater and groundwater | SOUTH SOMERSET | Yeovil Co Const | ST3724013020 | GB108052015170 | Dowlish Brook | DOWLISH BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 32 | 6 | 0 | 1 | 4.25 | 99.9857 | 11.4 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015170 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13101S | DRAYCOTT MILKING LANE STORM TANK | 070038 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | MENDIP | Wells Co Const | ST4721750393 | GB109052021570 | Axe - Cocklake to Brean Cross Sluice | DOLMEAD RHYNE(S) |  |  |  |  | Oct 2023 |  |  |  | 63 | 1203.1 | 100 |  | <1 yr (installed 2023) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021570 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13130S | FRESHFORD STORM TANK | 010037 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | Chippenham Co Const | ST7902960599 | GB109053027372 | Bristol Avon (Semington Bk to By Bk) | BRISTOL AVON |  |  |  |  | Commissioned in 2019 - full year data expected | 26 | 15 | 15 | 57 | 753.3974 | 100 | 28.25 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027372 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13139C | HALSE INLET | 012751 | Inlet SO at WwTW |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST1424028000 | GB108052021380 | Halse WTR | TRIBUTARY OF HALSE WATER(S) |  |  |  |  | Jul 2023 |  |  |  | 14 | 25.6367 | 99.9996 |  | <1 yr (installed 2023) | [7 empty] | 2021-05-17 | Lab assessment - No impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021380 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13201C | MARTOCK HURST BOW INLET | 100288 | Inlet SO at WwTW |  | Diluted | A combination of rainwater and groundwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST4512019240 | GB108052015350 | Wellhams Brook | PARRETT AND HINTON MEADS BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 54 | 38 | 29 | 19 | 92.3772 | 99.9125 | 27.1667 | 6 (installed 2017) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015350 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13205S | MELLS STORM TANK | 010059 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | MENDIP | Somerton and Frome Co Const | ST7339048896 | GB109053022020 | Mells source to conf with Somerset Frome | MELLS STREAM |  |  |  |  | Commissioned in 2017 - full year data expected | 47 | 2 | 14 | 25 | 271.5167 | 99.82 | 15.5714 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022020 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13211S | MILBORNE PORT VENN FARM STORM TANK | 102195 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST6836017440 | GB108052015630 | Yeo | HENOVER BROOK(S) |  |  |  |  | Commissioned in 2020 - full year data expected |  | 8 | 25 | 51 | 636.7333 | 99.9212 | 28 | 3 (installed 2020) | [5 empty] | 2023-10-20 | No sewage litter or sewage fungus | 2023-10-20 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015630 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13219S | NETHER STOWEY STORM TANK | 102162 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST2118240192 | GB108052021320 | Fiddington Brook | FIDDINGTON BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 17 | 13 | 13 | 47 | 471.25 | 99.9092 | 19.6 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021320 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13231S | OVER STRATTON OFF SOUTH HARP STORM TANK | 070085 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST4394314714 | GB108052015330 | Lopen Brook | LOPEN BROOK (S) |  |  |  |  | Commissioned in 2020 - full year data expected |  | 29 | 35 | 53 | 323.4667 | 99.9966 | 39 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015330 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13273B | SHIPTON GORGE OFF MARKETS LANE | NPSWQD008206 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | SY4985591135 | GB108044009550 | Bride | TRIBUTARY OF THE RIVER BRIDE |  |  |  |  | Aug 2023 |  |  |  | 10 | 64.8111 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009550 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13278S | SOMERTON BARPOOL LANE STORM TANK | 103392 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST4847029870 | GB108052015140 | Cary - source to conf with KSD | TRIB OF RIVER CARY() |  |  |  |  | Commissioned in 2020 - full year data expected |  | 31 | 47 | 89 | 1804.4333 | 99.7909 | 55.6667 | 3 (installed 2020) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015140 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13283B | SPAXTON | 070975 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST2412137369 | GB108052021310 | Cannington Bk - Lower | A TRIB OF THE CANNINGTON BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 13 | 11 | 6 | 13 | 150.25 | 99.9914 | 10.75 | 5 (installed 2018) | [9 empty] | 2021-11-12 | Inaccessible at time of visit |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021310 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13315S | TOCKINGTON MOOR LANE STORM TANK | 101834 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6006085880 | GB109054026650 | Chestle Pill | TOCKINGTON MILL RHINE(S) |  |  |  |  | Jan 2023 |  |  |  | 92 | 1888.7861 | 99.9238 |  | <1 yr (installed 2023) |  |  | Performance - Infiltration | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026650 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13318B | TROWBRIDGE BRADFORD ROAD INLET | 102153 | Inlet SO at WwTW |  | Diluted | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8491358447 | GB109053021791 | Biss (Bitham Bk to Bristol Avon) | F/E-RIVER AVON, CSO-RIVER BISS |  |  |  |  | Commissioned in 2019 - full year data expected | 21 | 10 | 12 | 17 | 125.0833 | 100 | 14 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021791 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13338S | WESTBURY STORM TANK | 101652 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8717252598 | GB109053021770 | Bitham Bk - source to conf Biss Bk | BITHAM BROOK/TRIB BITHAM BROOK |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 44 | 69 | 777 | 99.9996 | 56.5 | 2 (installed 2021) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021770 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13352S | WINSLEY STORM TANK | 102718 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | Chippenham Co Const | ST7948060070 | GB109053027372 | Bristol Avon (Semington Bk to By Bk) | RIVER AVON(S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 10 | 22 | 173.5833 | 100 | 16 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027372 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13514C | WEST BAGBOROUGH INLET | 071989 | Inlet SO at WwTW |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST1606033170 | GB108052021390 | Back Stream | TRIB OF BACK STREAM (TONE) (S) |  |  |  |  | Jul 2023 |  |  |  | 62 | 875.9158 | 100 |  | <1 yr (installed 2023) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021390 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13726C | BOURNEMOUTH CHARMINSTER ROAD NEAR 286-290 | Unpermitted | SO on sewer network |  | Diluted | Rainwater | BOURNEMOUTH | Bournemouth West Boro Const | SZ1333593666 | GB108043011040 | Stour (Lower) | Stour (Lower) |  |  |  |  | Nov 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011040 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14020B | LOWER STANTON DREW | 012370 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST5967063430 | GB109053021950 | Chew - conf Winford Bk to conf R Avon (Brist) | RIVER CHEW (S) |  |  |  |  | Aug 2023 |  |  |  | 6 | 9.3686 | 100 |  | <1 yr (installed 2023) | [9 empty] | 2021-12-09 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021950 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14057B | GREAT CHEVERELL CHEVERELL GREEN | 021366 | Storm discharge at pumping station |  | Diluted | Rainwater | KENNET | Devizes Co Const | ST9840054800 | GB109053022130 | Semington Bk - source to conf Worton Str | TRIB OF SEMINGTON BROOK (S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 13 | 16 | 101.6667 | 99.969 | 14.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022130 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14067B | BITTON | 010665 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6799069399 | GB109053027510 | Boyd - source to conf R Avon (Brist) | RIVER BOYD |  |  |  |  | Commissioned in 2017 - full year data expected | 17 | 14 | 7 | 16 | 145.7 | 99.5021 | 13.5 | 6 (installed 2017) | [9 empty] | 2021-10-25 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027510 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14072B | BLEADNEY BLEADNEY MILL | 102371 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | MENDIP | Wells Co Const | ST4860045430 | GB109052021520 | Axe - source to Cocklake | LOWER RIVER AXE(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 42 | 7 | 1 | 9 | 74.2333 | 99.7511 | 15.2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021520 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14075B | GLASTONBURY NORTH LOAD BRIDGE | 102496 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Wells Co Const | ST4936339519 | GB108052021190 | Brue - Clyce Hole to conf North Drain | GLASTONBURY MILL STREAM |  |  |  |  | Commissioned in 2018 - full year data expected | 17 | 13 | 1 | 4 | 26.0334 | 13.3883 | 8.75 | 5 (installed 2018) | Sensor failure / issue | Resolved - Dec | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021190 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14097C | BALTONSBOROUGH BALTONSBOROUGH MAIN 1 | 103055 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Somerton and Frome Co Const | ST5433034790 | GB108052021182 | Brue - Tootle Bridge to Clyse Hole | THE MILL STREAM(S) |  |  |  |  | Commissioned in 2020 - full year data expected | 2 | 0 | 51 | 57 | 263.2122 | 100 | 27.5 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021182 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14107B | WITHAM FRIARY | 102695 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Somerton and Frome Co Const | ST7463141192 | GB109053022080 | Frome - source to conf Maiden Bradley Bk | RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 16 | 9 | 14 | 36 | 299 | 99.8516 | 18 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022080 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14112B | WANSTROW | 102697 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Somerton and Frome Co Const | ST7135041860 | GB109053022000 | Nunney Bk - source to conf Mells R | TRIB OF THE NUNNEY BROOK(S) |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 10 | 29 | 139.55 | 99.8367 | 19.5 | 2 (installed 2021) | [9 empty] | 2021-11-30 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022000 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14114B | GLASTONBURY EDGARLEY MILLFIELD SCHOOL | 102378 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Wells Co Const | ST5197037680 | GB108052021130 | Coxbridge Brook( Brue) | TRIB OF UPPER RIVER BRUE |  |  |  |  | Commissioned in 2020 - full year data expected | 7 | 14 | 9 | 4 | 22.8667 | 99.9572 | 8.5 | 3 (installed 2020) | [9 empty] | 2022-05-09 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021130 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14125B | GILLINGHAM BUCKINGHAM ROAD | 042428 | Storm discharge at pumping station |  | Diluted | Rainwater | NORTH DORSET | North Dorset Co Const | ST8081026380 | GB108043022490 | Stour (Headwaters) | RIVER STOUR |  |  |  |  | Commissioned in 2018 - full year data expected | 17 | 14 | 17 | 42 | 213.5 | 99.9658 | 21 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022490 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14145B | MALMESBURY TANNERS BRIDGE | 103784 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9581187802 | GB109053027770 | Charlton Str - source to conf Bristol Avon | CHARLTON STREAM |  |  |  |  | Commissioned in 2018 - full year data expected | 6 | 10 | 19 | 70 | 1050.5833 | 99.9903 | 31.3333 | 5 (installed 2018) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue |  |  |  |  | 2022-04-14 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027770 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14157B | CALNE ROUGH LEAZE | 101356 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | SU0054668777 | GB109053022050 | Marden - source to conf Cowage Bk | RIVER MARDEN |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 28 | 34 | 693.1667 | 99.89 | 31 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022050 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14185B | MALMESBURY ST JOHNS STREET | 012855 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9361287083 | GB109053027780 | Tetbury Avon - unnamed trib to conf Sherston Avon | RIVER AVON (TETBURY BRANCH) |  |  |  |  | Commissioned in 2019 - full year data expected | 54 | 35 | 30 | 71 | 253.3705 | 100 | 44 | 4 (installed 2019) |  |  | Performance - Pump failure / issue | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027780 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14199B | UPPER MINETY FLISTERIDGE | 102549 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | SU0017091090 | GB106039023700 | Swill Brook (source to Ashton Keynes) | BRAYDON BROOK (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 30 | 19 | 23 | 46 | 676.25 | 99.7289 | 29.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB106039023700 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14260B | LYTCHETT MATRAVERS GLEBE ROAD | 041152 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | Mid Dorset and North Poole Co Const | SY9460994244 | GB108044010100 | Sherford River | TRIB OF SHERFORD RIVER |  |  |  |  | Commissioned in 2020 - full year data expected |  | 14 | 16 | 3 | 20.5167 | 21.627 | 11 | 3 (installed 2020) | Telemetry or data archiving failure / issue | Resolved - Dec | [7 empty] | 2022-02-10 | No impact (US 0.54mg/l, DS 0.51mg/l) |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010100 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14283B | BARTON ST DAVID | EPRCB3399AC | Storm discharge at pumping station |  | Diluted | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST5400333303 | GB108052021182 | Brue - Tootle Bridge to Clyse Hole | TRIBUTARY OF BARTON BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 19 | 9 | 48 | 27 | 247.7667 | 100 | 25.75 | 5 (installed 2018) |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021182 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14286B | LOPEN | NPSWQD004020 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | SOUTH SOMERSET | Yeovil Co Const | ST4272314017 | GB108052015330 | Lopen Brook | LOPEN BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 23 | 12 | 0 | 11 | 126.7167 | 99.9989 | 15.3333 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015330 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14375B | PEDWELL | 102298 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST4241736262 | GB108052021150 | King's Sedgemoor Drain - Henley Sluice to mouth | GREINTON RHYNE (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 16 | 20 | 17 | 26 | 94.2667 | 99.188 | 19.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021150 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14379B | FIDDINGTON | 102215 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST2173040660 | GB108052021320 | Fiddington Brook | FIDDINGTON BOOK(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 20 | 18 | 11 | 27 | 170.1936 | 96.718 | 19 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021320 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14384B | BRIDGWATER CHILTON STREET SALTLANDS | 102690 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST2996038050 | GB540805210900 | Parrett | RIVER PARRETT(TIDAL)(E) |  | BURNHAM JETTY NORTH | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=burnh&site=ukk2302-35300 |  | Commissioned in 2016 - full year data expected | 24 | 24 | 19 | 37 | 46.2035 | 99.9995 | 18.25 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB540805210900 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14392B | WEST BUCKLAND | 101804 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST1788020900 | GB108052015400 | Hele Bk | TRIB OF RIVER TONE (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 23 | 15 | 8 | 7 | 57.5 | 99.9935 | 13.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015400 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14427B | HALLATROW | 101867 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6398057270 | GB109053022290 | Cam Bk - source to conf Wellow Bk | CAM BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 26 | 10 | 12 | 20 | 112.8808 | 99.9943 | 17 | 5 (installed 2018) | [9 empty] | 2021-12-13 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022290 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14450B | COULSTON | 103785 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST9504054440 | GB109053022140 | Bulkington Drove w/c source to conf Semington Bk | A TRIB OF THE SEMINGTON BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 14 | 28 | 196.3667 | 99.7896 | 21 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022140 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14456B | BRATTON TROWBRIDGE ROAD | 103243 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST9099052800 | GB109053021770 | Bitham Bk - source to conf Biss Bk | TRIB OF BITHAM BROOK |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 10 | 15 | 58.2167 | 99.9677 | 12.5 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021770 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14457B | BULKINGTON WICKLEAZE | 011485 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST9436758258 | GB109053022170 | Semington Brook (Worton Str to Milebourne Str | TRIBUTARY OF SEMINGTON BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 17 | 5 | 14 | 21 | 265.7667 | 99.621 | 14.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022170 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14466B | SEMINGTON SEMINGTON BROOK | 102810 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | WEST WILTSHIRE | Chippenham Co Const | ST8988060810 | GB109053022200 | Semington Bk-Milebourne Str to conf R Avon (Brist) | SEMINGTON BROOK (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 19 | 12 | 18 | 23 | 259.5 | 99.9658 | 18 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022200 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14468B | MELKSHAM SEMINGTON ROAD | 100635 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | Chippenham Co Const | ST9014062340 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | (S) BERRYFIELD BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 15 | 18 | 160.9167 | 100 | 16.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14475B | BROUGHTON GIFFORD THE GREEN | 100634 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | Chippenham Co Const | ST8770162982 | GB109053021890 | Chalfield Brook - source to conf Avon | TRIB OF CHALFIELD BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 11 | 25 | 274.15 | 100 | 18 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021890 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14490C | EDINGTON TINHEAD LOWER BAYNTON ROAD | 011492 | Storm discharge at pumping station |  | Diluted | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST9340054000 | GB109053022150 | MIlebourne Str - source to conf Semington Bk | TRIB OF BUCKINGTON DROVE |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 27 | 54 | 276.3472 | 100 | 40.5 | 1 (installed 2022) | [5 empty] | 2020-11-26 | No sewage litter or sewage fungus | 2020-11-26 | Lab assessment - Impact |  |  |  | RICT analysis complete (Impact high) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022150 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14528B | CARLINGCOTT STONEAGE LANE | 013269 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6962058500 | GB109053022290 | Cam Bk - source to conf Wellow Bk | CAM BROOK (S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 15 | 31 | 268.15 | 99.9722 | 23 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022290 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14533C | MIDSOMER NORTON CAUTLETTS CLOSE | 011552 | SO on sewer network |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6583753584 | GB109053022251 | Somer | RIVER SOMER |  |  |  |  | Commissioned in 2022 - full year data expected |  |  |  | 23 | 281.4333 | 99.0297 | 23 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022251 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14542B | COAT CRIPPLE STREET (OLD STW SITE) | 071742 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST4509220512 | GB108052015360 | Parrett - Lopen Bk to R Isle | TRIBUTARY OF THE RIVER PARRETT |  |  |  |  | Commissioned in 2018 - full year data expected | 35 | 27 | 27 | 22 | 97.5667 | 99.9994 | 27 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015360 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14558C | COMPTON DURVILLE STORM SCREEN | 102006 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST4197017550 | GB108052015340 | Lam Brook | TRIB OF LAMBROOK BROOK(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 19 | 11 | 17 | 28 | 82.7061 | 99.9475 | 18.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015340 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14580B | BRISTOL ULLSWATER CLOSE | 103824 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6763072930 | GB109053027450 | Siston Bk - source to conf R Avon (Brist) | A TRIB OF THE SISTON BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 99.9996 | 0 | 1 (installed 2022) | [9 empty] | 2022-11-09 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027450 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14589C | YEOVIL UNIT 5 YEO LEISURE PARK | EPRTB3591NX | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5639515975 | GB108052015600 | Dodham Brook (Yeo (Somset)) | DODHAM BROOK VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  |  | 13 | 26.5333 | 99.7949 | 13 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015600 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14590C | YEOVIL UNIT 4 YEO LEISURE PARK | EPRTB3591EY | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5639515975 | GB108052015600 | Dodham Brook (Yeo (Somset)) | DODHAM BROOK VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  |  | 7 | 9.3333 | 99.8817 | 7 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015600 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15075B | CORFE MULLEN PARDYS HILL | 401392 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | EAST DORSET | Mid Dorset and North Poole Co Const | SY9830097600 | GB108043016052 | Stour (Middle d/s Pimperne Brook) | TRIB OF RIVER STOUR(S) |  |  |  |  | Commissioned in 2020 - full year data expected | 18 | 12 | 18 | 26 | 115 | 98.9562 | 18.5 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016052 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15125B | WORTON MILL ROAD | 102479 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | KENNET | Devizes Co Const | ST9657057540 | GB109053022170 | Semington Brook (Worton Str to Milebourne Str | SEMINGTON BROOK (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 18 | 9 | 19 | 22 | 193.05 | 99.7733 | 17 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022170 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15139B | PILNING SWANMOOR BRIDGE | 101958 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Filton and Bradley Stoke Co Const | ST5651083380 | GB109054026650 | Chestle Pill | SWANMOOR RHINE (S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 100 | 0 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026650 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15189B | AUST VILLAGE | 010692 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST5743088975 | 139 | Not part of a river WB catchment | FOSS DITCH |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 12 | 43 | 705.5333 | 99.7808 | 27.5 | 1 (installed 2022) | [13 empty] | Not part of a river WB catchment | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15193B | CHILD OKEFORD GOLD HILL | 402218 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH DORSET | North Dorset Co Const | ST8280013550 | GB108043016051 | Stour (Middle u/s Pimperne Brook) | TRIB OF RIVER STOUR(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 14 | 14 | 3 | 1 | 0.25 | 100 | 8 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016051 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15196B | STURMINSTER NEWTON THE BRIDGE | 402224 | Storm discharge at pumping station |  | Diluted | Rainwater | NORTH DORSET | North Dorset Co Const | ST7860013680 | GB108043016051 | Stour (Middle u/s Pimperne Brook) | THE RIVER STOUR(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 17 | 9 | 18 | 19 | 128.3667 | 100 | 15.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016051 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15306B | LOWER SOMERTON | 102063 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST4975128348 | GB108052015140 | Cary - source to conf with KSD | MILLSTREAM |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 15 | 23 | 207.0333 | 99.7884 | 19 | 2 (installed 2021) | [5 empty] | 2021-11-02 | No sewage litter or sewage fungus | [6 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015140 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15314B | UPTON NR LANGPORT | 102405 | Storm discharge at pumping station |  | Diluted and partially treated | A combination of rainwater and groundwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST4585726067 | GB108052021150 | King's Sedgemoor Drain - Henley Sluice to mouth | TRIB OF LONG SUTTON MAIN DRAIN |  |  |  |  | Commissioned in 2020 - full year data expected | 17 | 8 | 9 | 20 | 170.1 | 99.9962 | 13.5 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021150 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15318C | STOFORD HILLSIDE MAIN | 070149 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5676014140 | GB108052015590 | Sutton Bingham Stream - conf Closworth Str to conf Yeo | YEOVIL YEO,TRIB OF THE (S) |  |  |  |  | Commissioned in 2020 - full year data expected |  | 14 | 25 | 26 | 214.8833 | 98.8295 | 21.6667 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015590 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15322B | PITNEY | 103180 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST4412228450 | GB108052021150 | King's Sedgemoor Drain - Henley Sluice to mouth | TRIBUTARY OF LOW HAM RHYNE |  |  |  |  | Commissioned in 2019 - full year data expected | 51 | 40 | 26 | 68 | 1115.4333 | 98.2042 | 46.25 | 4 (installed 2019) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue |  |  |  |  | 2022-03-01 | Impact (US 0.23mg/l, DS 0.44mg/l) |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021150 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15325B | KEINTON MANDEVILLE | 103181 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST5489029692 | GB108052015140 | Cary - source to conf with KSD | TRIB OF RIVER CAREY(VIA DRAIN) |  |  |  |  | Commissioned in 2020 - full year data expected |  | 26 | 13 | 19 | 132.7833 | 99.9842 | 19.3333 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015140 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15393B | BRIDGWATER TAUNTON ROAD | 102692 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3051035800 | GB540805210900 | Parrett | RIVER PARRETT(TIDAL)(E) |  | BURNHAM JETTY NORTH | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=burnh&site=ukk2302-35300 |  | Commissioned in 2016 - full year data expected | 11 | 18 | 27 | 34 | 62.2089 | 100 | 21.25 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB540805210900 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15397B | STAWELL FORD LANE | 101711 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3671038610 | GB108052021150 | King's Sedgemoor Drain - Henley Sluice to mouth | TRIB OF KING SEDGEMOORS DRAIN |  |  |  |  | Commissioned in 2018 - full year data expected | 12 | 23 | 4 | 11 | 42.8 | 100 | 12.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021150 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15439B | HENLADE | NPSWQD001440 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST2660723569 | GB108052015420 | Broughton Brook (South and West Somerset) | TRIBUTARY OF BLACK BROOK |  |  |  |  | Commissioned in 2020 - full year data expected |  | 18 | 2 | 34 | 457.9 | 98.5242 | 18 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015420 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15446B | HILLCOMMON HILL COMMON | NPSWQD003671 | Storm discharge at pumping station |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST1525826020 | GB108052015481 | Tone - Wellington to Taunton | TRIBUTARY OF RIVER TONE |  |  |  |  | Commissioned in 2020 - full year data expected |  | 16 | 9 | 7 | 24.55 | 99.9482 | 10.6667 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015481 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15459B | RUMWELL | 082085 | Storm discharge at pumping station |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST1940023620 | GB108052015400 | Hele Bk | UNNAMED STREAM |  |  |  |  | Jul 2023 |  |  |  | 0 | 0 | 99.9718 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015400 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15481B | BRADPOLE LEE LANE | 402029 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | SY4808993847 | GB108044009580 | Asker | RIVER ASKER |  |  |  |  | Commissioned in 2018 - full year data expected | 13 | 9 | 13 | 25 | 142.75 | 97.911 | 13.8 | 5 (installed 2018) | [9 empty] | 2021-11-17 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009580 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15496B | LEIGH BRIDGE FARM | 102978 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | ST6231808442 | GB108052015580 | Beer Hackett Stream | TRIB OF RIVER WRIGGLE |  |  |  |  | Commissioned in 2020 - full year data expected |  | 17 | 14 | 18 | 107.4167 | 94.6426 | 16.3333 | 3 (installed 2020) | [9 empty] | 2022-02-16 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015580 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15511B | MONKSILVER B3188 | 102301 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | ST0722037610 | GB108051020260 | Monksilver Stream | MONKSILVER STREAM (S) |  |  |  |  | Commissioned in 2020 - full year data expected | 16 | 19 | 7 | 30 | 447.6132 | 99.8937 | 18 | 3 (installed 2020) | [9 empty] | 2021-11-12 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108051020260 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15523B | CAMERTON SUNNYVALE | 021687 | Storm discharge at pumping station |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6799857877 | GB109053022290 | Cam Bk - source to conf Wellow Bk | TRIBUTARY OF MIDFORD BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 100 | 0 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022290 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15535B | PEASEDOWN ST JOHN NEW BUILDINGS / WHITEBROOK LANE | 103600 | Storm discharge at pumping station |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6944057350 | GB109053022290 | Cam Bk - source to conf Wellow Bk | UNNAMED DITCH(S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  |  | 26 | 33.6369 | 99.999 | 26 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022290 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15537B | SHOSCOMBE SINGLE HILL | 021446 | Storm discharge at pumping station |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST7209056220 | GB109053022271 | Wellow Bk - Snails Bk to Bristol Avon | A TRIBUTARY OF WELLOW BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  |  | 0 | 0 | 99.9992 | 0 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022271 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15569B | PORTBURY DROVE | 070828 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH SOMERSET | North Somerset Co Const | ST4994076070 | 140 | Not part of a river WB catchment | PORTBURY DROVE RHYNE |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 100 | 0 | 1 (installed 2022) | [13 empty] | Not part of a river WB catchment | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15691C | MOTCOMBE TANK (PUMPED) | 042071 | Storm discharge at pumping station |  | Diluted | Rainwater | NORTH DORSET | North Dorset Co Const | ST8492025530 | GB108043022440 | Lodden | TRIBUTARY OF RIVER LODDEN (S) |  |  |  |  | Commissioned in 2020 - full year data expected |  | 13 | 22 | 29 | 278.4958 | 99.9877 | 21.3333 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022440 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15772B | PEASEDOWN ST JOHN WELLOW LANE | 103787 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST7156057060 | GB109053022271 | Wellow Bk - Snails Bk to Bristol Avon | A TRIB OF THE WELLOW BROOK |  |  |  |  | Aug 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022271 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16042C | BATH SOUTH PARADE IN GARDEN | 102819 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7539064613 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2017 - full year data expected | 21 | 20 | 19 | 22 | 179.4167 | 99.4696 | 17 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16046C | BATH FERRY LANE O/S FUNERAL DIRECTOR | 101227 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7541064580 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 20 | 14 | 11 | 14 | 11.7333 | 99.7002 | 15.2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16060C | BATH SPRING GARDENS ROAD NO 1 | 103041 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7540064500 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON(S) |  |  |  |  | Feb 2023 |  |  |  | 18 | 101.1 | 99.9985 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16062C | BATH WALCOT SYPHON AT HEAD | 103042 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7514365181 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | THE RIVER AVON |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 4 | 5 | 27.2333 | 99.9467 | 4.5 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16070C | BATH WALCOT ST RIVER BANK R/O ALDRIDGES | 103044 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7520965488 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 33 | 23 | 21 | 24 | 13.2667 | 99.9121 | 17.625 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16072C | BATH ST JOHNS ROAD SCOUTS SITE | 101188 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7531365593 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 20 | 18 | 8 | 19 | 66.6667 | 82.2595 | 11.375 | 5 (installed 2018) | Sensor failure / issue | Resolved - Dec |  |  |  | 2021-03-29 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16073C | BATH CLEVELAND BRIDGE TO THE WEST | 010862 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7531465649 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 23 | 14 | 9 | 11 | 0.66667 | 99.9631 | 12.625 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16077C | BATH WALCOT TERRACE R/O NO 1 ON LONDON ROAD | 100679 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7537465704 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 21 | 17 | 11 | 17 | 40.5333 | 99.6686 | 12.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16078C | BATH FORESTER AVENUE O/S HORTON HOUSE | 101189 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7541665700 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 26 | 22 | 16 | 22 | 27.0667 | 97.3021 | 17 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16088C | BATH PARADE GARDENS | 021513 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7528264806 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 21 | 15 | 20 | 25 | 222.6667 | 99.7534 | 16.625 | 5 (installed 2018) | [5 empty] | 2022-03-15 | No sewage litter or sewage fungus |  | N/A | 2022-03-01 | Water Quality Modelling shows that the WFD Status Class at the 99%ile level for BOD and Ammonia is High ‘with’ or ‘without’ all Bath FSOs |  | Incomplete - need boat for access | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16152C | BRISTOL FLOWERS HILL TRADING ESTATE | 100582/CS/01 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6199270650 | GB109053021980 | Brislington Bk - source to conf R Avon (Brist) | BRISLINGTON BROOK VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 18 | 14 | 10 | 7 | 0.8 | 99.5654 | 12.25 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021980 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16156C | BRISTOL BRISLINGTON HILL/BRISTOL HILL JNC. | 012935 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6198070709 | GB109053021980 | Brislington Bk - source to conf R Avon (Brist) | BRISLINGTON BROOK VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 13 | 18 | 11 | 20 | 32.2667 | 98.0183 | 17 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021980 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16174C | BRISTOL SOMERDALE AVENUE / SPRING GARDENS | 100575/CS/01 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST6027469895 | GB109053021980 | Brislington Bk - source to conf R Avon (Brist) | BRISLINGTON BROOK VIA SWS |  |  |  |  | Commissioned in 2021 - full year data expected |  | 17 | 12 | 21 | 12.0833 | 99.9873 | 16.6667 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021980 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16179C | BRISTOL WELLS ROAD O/S NO 395 | 013221 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST6092269972 | GB109053021980 | Brislington Bk - source to conf R Avon (Brist) | BRISLINGTON BROOK |  |  |  |  | Aug 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021980 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16180C | BRISTOL WELLS ROAD O/S NO 424 | 013222 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST6090369971 | GB109053021980 | Brislington Bk - source to conf R Avon (Brist) | BRISLINGTON BROOK VIA SWS |  |  |  |  | Jan 2023 |  |  |  | 37 | 12.5667 | 99.8447 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021980 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16181C | BRISTOL WELLS ROAD / PRIORY ROAD | 013220 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST6092269972 | GB109053021980 | Brislington Bk - source to conf R Avon (Brist) | BRISLINGTON BROOK |  |  |  |  | Jan 2023 |  |  |  | 0 | 0 | 99.7549 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021980 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16185C | BRISTOL WOOTTON PARK | 100578/CS/01 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST6099169999 | GB109053021980 | Brislington Bk - source to conf R Avon (Brist) | BRISLINGTON BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 99.7549 | 0 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021980 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16199C | BRISTOL NELSON STREET O/S POLICE STATION | 101084 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5895173265 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME |  |  |  |  | Apr 2023 |  |  |  | 0 | 0 | 99.7546 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16247C | BRISTOL MOORLANDS ROAD O/S NO 63 | 101236 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6233074960 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | COOMBE BROOK(S) |  |  |  |  | Aug 2023 |  |  |  | 12 | 1.7 | 98.8174 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16260C | BRISTOL ANDOVER ROAD / STOCKWOOD CRESCENT | 101819 | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol South Boro Const | ST5973170538 | GB109053021970 | The Malago - source to conf R Avon (Brist New Cut) | TRIBUTARY OF THE MALAGO |  |  |  |  | Feb 2023 |  |  |  | 6 | 1.0333 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021970 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16268C | BRISTOL DERHAM ROAD R/O NO 31 | 101820 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST5729768434 | GB109053021970 | The Malago - source to conf R Avon (Brist New Cut) | TRIB OF THE MALAGO |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 1 | 5.1 | 100 | 0.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021970 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16280C | BRISTOL OLD MEAD WALK NO 9 | 101818 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST5617669091 | 157 | Not part of a river WB catchment | TRIB . COLLITERS BROOK VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 13 | 3 | 1.4333 | 91.2123 | 8 | 1 (installed 2022) | [13 empty] | Not part of a river WB catchment | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16285C | BRISTOL ST JOHNS LANE | 101671 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST5849170828 | GB109053021970 | The Malago - source to conf R Avon (Brist New Cut) | THE MALAGO (S) |  |  |  |  | Sep 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021970 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16291C | BRISTOL BIRCHALL ROAD O/S NO 1 | 100874 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5860075080 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | (S) CRANBROOK |  |  |  |  | Nov 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16313C | BRISTOL ST OSWALDS ROAD NO 2 IN BACK GARDEN | 100871 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5793475224 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | TRIB OF CRANBROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 3 | 0.53333 | 99.7306 | 1.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16317C | BRISTOL CHAPLIN ROAD O/S NO 60 | 101792 | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol West Boro Const | ST6042874443 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 11 | 5 | 2.1333 | 89.2169 | 8 | 1 (installed 2022) | Sensor failure / issue | Resolved - Jul | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16361C | BRISTOL THE MANSE SUMMERS LANE | 101726 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST6011674254 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME (S) |  |  |  |  | Jan 2023 |  |  |  | 7 | 12.8667 | 99.8712 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16363C | BRISTOL TORTWORTH ROAD | NPSWQD010488 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5997776032 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | HORFIELD BROOK |  |  |  |  | Commissioned in 2020 - full year data expected |  | 28 | 7 | 0 | 0 | 99.9068 | 11.6667 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16419C | BRISTOL MULLER ROAD / FROME BRIDGE | 101746 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST6105575260 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME |  |  |  |  | Commissioned in 2020 - full year data expected |  | 24 | 15 | 17 | 4.5 | 99.6533 | 18.6667 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16451C | DEVIZES ROUNDWAY HOSPITAL | 102809 | SO on sewer network |  | Diluted | Rainwater | KENNET | Devizes Co Const | SU0094059670 | GB109053022190 | Poulshot Str - source to conf Summerham Bk | SUMMERHAM BROOK (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 23 | 6 | 2 | 5 | 3.25 | 87.9657 | 9 | 5 (installed 2018) | Telemetry or data archiving failure / issue | Resolved - Feb | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022190 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16453C | LITTLETON PANELL RUSSELL MILL LANE | 101766 | SO on sewer network |  | Diluted | Rainwater | KENNET | Devizes Co Const | SU0015454163 | GB109053022130 | Semington Bk - source to conf Worton Str | SEMINGTON BROOK VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 12 | 10 | 19 | 17 | 4.6667 | 93.6256 | 14.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022130 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16464C | BRISTOL HANHAM CENTRAL AVENUE | 101754 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6433670901 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | TRIB OF RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 10 | 17 | 9 | 19 | 9.1667 | 99.8124 | 13.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16478C | BRISTOL KINGSWOOD DOWNEND ROAD NO 48 | 100892 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6631974374 | GB109053027450 | Siston Bk - source to conf R Avon (Brist) | WARMLEY BROOK VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected |  | 22 | 16 | 71 | 54.7333 | 99.9745 | 36.3333 | 3 (installed 2020) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027450 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16480C | BRISTOL KINGSWOOD NEW CHELTENHAM ROAD O/S 23 / 25 | 100894 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6631974374 | GB109053027450 | Siston Bk - source to conf R Avon (Brist) | WARMLEY BROOK(S) |  |  |  |  | Sep 2023 |  |  |  | 4 | 2.6667 | 99.9745 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027450 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16497C | BALTONSBOROUGH ORCHARD LEIGH | 101888 | SO on sewer network |  | Diluted | A combination of rainwater and groundwater | MENDIP | Somerton and Frome Co Const | ST5454834384 | GB108052021182 | Brue - Tootle Bridge to Clyse Hole | MILL STREAM(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 26 | 10 | 10 | 12 | 67.1333 | 100 | 12.2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021182 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16503C | FROME FELTHAM DRIVE NEAR FOOTBRIDGE | 100439 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Somerton and Frome Co Const | ST7787547072 | GB109053022101 | Frome (Maiden Bradley to Mells) | ADDERWELL BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 26 | 16 | 9 | 16 | 1.4 | 99.7759 | 15.125 | 5 (installed 2018) | [5 empty] | 2019-08-01 | No sewage litter or sewage fungus | [5 empty] | No sewage fungus assessment | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022101 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16504C | FROME MERCHANTS BARTON | 100440 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Somerton and Frome Co Const | ST7784448085 | GB109053022101 | Frome (Maiden Bradley to Mells) | RIVER FROME (VIA SWS) |  |  |  |  | Commissioned in 2017 - full year data expected | 17 | 20 | 13 | 24 | 6.2 | 96.1807 | 15.125 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022101 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16510C | FROME PORTWAY / LOCKS HILL | 102702 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Somerton and Frome Co Const | ST7865147772 | GB109053022101 | Frome (Maiden Bradley to Mells) | RIVER FROME |  |  |  |  | Apr 2023 |  |  |  | 15 | 3.0333 | 99.954 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022101 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16513C | FROME RODDEN ROAD | 102704 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Somerton and Frome Co Const | ST7828048134 | GB109053022101 | Frome (Maiden Bradley to Mells) | RIVER FROME(VIA SWS) |  |  |  |  | Commissioned in 2018 - full year data expected | 31 | 20 | 8 | 6 | 3 | 99.7287 | 15.375 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022101 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16526C | SHEPTON MALLET CATS ASH/COWL STREET | 100506 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Wells Co Const | ST6183043830 | GB108052021221 | Sheppey | RIVER SHEPPEY |  |  |  |  | Commissioned in 2017 - full year data expected | 17 | 16 | 10 | 17 | 2.5 | 99.7538 | 15.3333 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021221 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16527C | SHEPTON MALLET SUNNY MOUNT/HAM LANE | 103409 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Wells Co Const | ST6115043990 | GB108052021221 | Sheppey | RIVER SHEPPEY |  |  |  |  | Commissioned in 2018 - full year data expected | 18 | 16 | 13 | 16 | 10.0667 | 71.6724 | 13.3333 | 5 (installed 2018) | Sensor failure / issue | Resolved - Dec | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021221 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16543C | WELLS PRIORY HOSPITAL IN THE REAR GARDEN NEAR WEIR | 100749 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Wells Co Const | ST5425545263 | GB108052021240 | Keward Brook | ST ANDREWS STREAM |  |  |  |  | Commissioned in 2018 - full year data expected | 18 | 18 | 13 | 23 | 25.7667 | 95.2097 | 17.3333 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021240 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16544C | WOOKEY HOLE KENNEL BATCH / HIGH STREET | 102374 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Wells Co Const | ST5313247317 | GB109052021520 | Axe - source to Cocklake | TRIB OF RIVER AXE VIA SWS |  |  |  |  | Apr 2023 |  |  |  | 5 | 12.5333 | 99.9745 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021520 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16550C | GILLINGHAM QUEEN STREET | 402123 | SO on sewer network |  | Diluted | Rainwater | NORTH DORSET | North Dorset Co Const | ST8073326661 | GB108043022450 | Shreen Water (including Ashfield Water) | SHREEN WATER |  |  |  |  | Commissioned in 2020 - full year data expected |  | 10 | 13 | 11 | 52.7 | 71.3908 | 11.3333 | 3 (installed 2020) | Capital / maintenance works affect EDM operation | Scheduled | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022450 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16552C | STURMINSTER NEWTON BULL INN | 400807 | SO on sewer network |  | Diluted | Rainwater | NORTH DORSET | North Dorset Co Const | ST7853013574 | GB108043016051 | Stour (Middle u/s Pimperne Brook) | RIVER STOUR |  |  |  |  | Commissioned in 2020 - full year data expected | 10 | 12 | 22 | 27 | 228.3667 | 100 | 17.75 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016051 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16555C | FRAMPTON COTTERELL ST PETERS CHURCH (SE) BRIDGE WAY | 101033 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6675681889 | GB109053027820 | Frome (Brist) - conf Laddon Bk to conf Folly Bk | RIVER FROME |  |  |  |  | Commissioned in 2019 - full year data expected | 28 | 7 | 2 | 2 | 0.16667 | 99.9889 | 9.5714 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027820 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16559C | PUCKLECHURCH FELTHAM ROAD | 103912 | SO on sewer network |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST7032076470 | GB109053027510 | Boyd - source to conf R Avon (Brist) | TRIBUTARY OF FELTHAM BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 21 | 20 | 15 | 50 | 441 | 99.9239 | 26.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027510 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16564C | CHIPPENHAM BRISTOL ROAD | 100818 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | Chippenham Co Const | ST9114273900 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | HARDENHUISH BROOK |  |  |  |  | Jan 2023 |  |  |  | 63 | 93.5667 | 99.5126 |  | <1 yr (installed 2023) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16572C | CHIPPENHAM DALLAS ROAD | 100821 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | Chippenham Co Const | ST9168773636 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | HARDENHUISH BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 99.4441 | 0 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16583C | MALMESBURY LOWER HIGH STREET | 012851 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9352386908 | GB109053027690 | Sherston Avon | SHERSTON AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 33 | 26 | 20 | 40 | 149.8 | 93.9144 | 26 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027690 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16588C | CALNE MOSSES MILL 2 | 100773 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9877070738 | GB109053022050 | Marden - source to conf Cowage Bk | RIVER MARDEN |  |  |  |  | Feb 2023 |  |  |  | 50 | 222.2333 | 99.9235 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022050 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16589C | ROYAL WOOTTON BASSETT NEAR STW | 103417 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | SU0731181464 | GB109053027740 | Brinkworth Brook | HANCOCK'S WATER |  |  |  |  | Commissioned in 2018 - full year data expected | 22 | 12 | 8 | 35 | 125.2333 | 99.6872 | 15.6667 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027740 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16590C | CALNE RIVER MARDEN (RIVER BANK) SOUTH MARDEN HOUSE NEW ROAD | 100776 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9967570740 | GB109053022050 | Marden - source to conf Cowage Bk | RIVER MARDEN |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 2 | 1.2667 | 99.7549 | 1 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022050 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16594C | MALMESBURY PARK ROAD | 012853 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9277687856 | GB109053027780 | Tetbury Avon - unnamed trib to conf Sherston Avon | RIVER AVON (TETBURY BRANCH) |  |  |  |  | Commissioned in 2018 - full year data expected | 2 | 27 | 25 | 38 | 32.5 | 95.7839 | 15.6667 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027780 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16601C | CALNE STRAND / CHURCH STREET | 100715 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9970070751 | GB109053022050 | Marden - source to conf Cowage Bk | RIVER MARDEN |  |  |  |  | Commissioned in 2019 - full year data expected | 22 | 15 | 13 | 22 | 9.0667 | 99.8307 | 17.8 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022050 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16606C | CHIPPENHAM WOOD LANE | 102554 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | Chippenham Co Const | ST9219672647 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | TRIBUTARY OF RIVER AVON |  |  |  |  | Jan 2023 |  |  |  | 7 | 13.75 | 99.8423 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16608C | MALMESBURY PARLIAMENT ROW | EPRJB3797NC | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9353486763 | GB109053027690 | Sherston Avon | RIVER AVON (SHERSTON BRANCH) |  |  |  |  | Jan 2023 |  |  |  | 23 | 19.4333 | 99.7751 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027690 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16611C | CALNE MARKET HILL / STRAND | 100771 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9969870751 | GB109053022050 | Marden - source to conf Cowage Bk | RIVER MARDEN VIA SWS |  |  |  |  | Jan 2023 |  |  |  | 2 | 0.43333 | 99.7549 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022050 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16662C | CANNINGTON MARSH LANE | 102214 | SO on sewer network |  | Diluted | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST2631039810 | GB108052021310 | Cannington Bk - Lower | TRIB OF CANNINGTON BROOK(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 8 | 20 | 17 | 31 | 90.7667 | 99.8546 | 17 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021310 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16664C | CHEDDAR HELLIER LANE / LOWER NEW ROAD | 101666 | SO on sewer network |  | Diluted | Rainwater | SEDGEMOOR | Wells Co Const | ST4509853342 | GB109052021540 | Cheddar Yeo - source to conf Stubbingham Rhyne | HELLIERS STREAM VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected |  | 14 | 8 | 16 | 109.9333 | 99.9715 | 12.6667 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021540 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16670C | CASTLE CARY TORBAY ROAD | 071725 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST6335032400 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER CARY |  |  |  |  | Sep 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16671C | CREWKERNE HENHAYES | 101657 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST4507009660 | GB108052015260 | Parrett - headwaters to Broad River | CREWKERNE STREAM(S) |  |  |  |  | Commissioned in 2019 - full year data expected | 16 | 14 | 9 | 20 | 9.75 | 99.9971 | 14.75 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015260 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16679C | STOKE SUB HAMDON NORTH STREET O/S NO 50 | 100711 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST4737717602 | GB108052015350 | Wellhams Brook | TRIB OF THE WELLHAMS BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 19 | 21 | 19 | 54 | 52.8667 | 100 | 28.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015350 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16681C | MARTOCK HURST NO 22 | 013156 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST4573318639 | GB108052015350 | Wellhams Brook | TRIB OF HINTON MEADS BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 12 | 5 | 21 | 30 | 38.1 | 99.9745 | 17 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015350 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16708C | TEMPLECOMBE ROYAL HOTEL | 040122 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST7099722602 | GB108043015820 | Bow Brook North | TRIB OF BOW BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 15 | 17 | 19 | 19 | 19.9333 | 99.7523 | 17.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015820 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16709C | LANGPORT SOMERTON ROAD | 102571 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST4200227090 | GB108052021150 | King's Sedgemoor Drain - Henley Sluice to mouth | NORTHSTREET MOOR RHYNE VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 20 | 16 | 24 | 32 | 33.2667 | 99.7782 | 23 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021150 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16717C | WINCANTON MOOR LANE | 041687 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST7130227880 | GB108043015850 | Cale | TRIB OF RIVER CALE VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 13 | 24 | 113.4 | 99.9985 | 18.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015850 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16725C | WOTTON-UNDER-EDGE WATER LANE | 103418 | SO on sewer network |  | Diluted | Rainwater | STROUD | The Cotswolds Co Const | ST7592793130 | GB109054026610 | Ozleworth Bk - source to conf Little Avon R | DYERS BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 29 | 25 | 19 | 42 | 23.8667 | 99.6183 | 23 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026610 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16726C | WOTTON-UNDER-EDGE OLD COACH YARD | 103419 | SO on sewer network |  | Diluted | Rainwater | STROUD | The Cotswolds Co Const | ST7596493210 | GB109054026610 | Ozleworth Bk - source to conf Little Avon R | DYERS BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 25 | 12 | 22 | 24 | 5.5333 | 92.0396 | 19 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026610 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16746C | MILVERTON HOUNDSMOOR LANE | 102263 | SO on sewer network |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST1267125872 | GB108052015510 | Hillfarrance Bk | TRIB OF HILLFARRANCE BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 14 | 20 | 9 | 100 | 17 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015510 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16757C | BATHEASTON MILL HOUSE | 021669 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST7785067930 | GB109053027810 | St Catherines Bk - source to conf R Avon (Brist) | TRIB OF RIVER BRISTOL AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 24 | 15 | 9 | 25 | 23.4 | 99.7203 | 18.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027810 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16782C | CLUTTON MAYPOLE FARM | 103315 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6219259182 | GB109053022290 | Cam Bk - source to conf Wellow Bk | TRIB OF THE CAM BROOK |  |  |  |  | Commissioned in 2020 - full year data expected |  | 23 | 15 | 20 | 12.2667 | 99.753 | 19.3333 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022290 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16786C | PAULTON PAULTON WORKS OFF BRISTOL ROAD | 102213 | SO on sewer network |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6526257063 | GB109053022290 | Cam Bk - source to conf Wellow Bk | TRIB OF CAM BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 27 | 19 | 20 | 41 | 121.2667 | 99.9987 | 22 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022290 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16803C | SHERBORNE ABBEY ROAD | NPSWQD002501 | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | ST6370816577 | GB108052015630 | Yeo | TRIBUTARY OF THE RIVER YEO |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 11 | 11 | 5.5667 | 100 | 11 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015630 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16804C | SHERBORNE CHEAP STREET | EPRJB3795WW | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | ST6352816864 | GB108052015630 | Yeo | TRIB OF THE RIVER YEO VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected |  | 10 | 12 | 10 | 3.8 | 99.7508 | 10.6667 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015630 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16815C | BEAMINSTER HAMS PLOT SOUTH GATE | 401558 | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | ST4799401077 | GB108044009600 | Brit (Upper) | RIVER BRIT(S) |  |  |  |  | Commissioned in 2020 - full year data expected |  | 16 | 7 | 10 | 29.5333 | 100 | 11 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009600 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16821C | BRIDPORT WEST BRIDGE | 402082 | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | SY4627093030 | GB108044009600 | Brit (Upper) | RIVER BRIT |  |  |  |  | Commissioned in 2017 - full year data expected | 13 | 18 | 5 | 12 | 43.7667 | 94.4802 | 10.6667 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009600 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16828C | CLEVEDON OLD STREET O/S 46 | 102297 | SO on sewer network |  | Diluted | Rainwater | NORTH SOMERSET | North Somerset Co Const | ST4116071220 | GB109052027321 | Land Yeo - Yearling Ditch to mouth | LAND YEO (S) |  |  |  |  | Nov 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052027321 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16877C | COWBRIDGE COWBRIDGE SO | 102302 | SO on sewer network |  | Diluted | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | SS9583342806 | GB108051020210 | Avill | RIVER AVILL |  |  |  |  | Commissioned in 2018 - full year data expected | 33 | 14 | 16 | 17 | 48.2 | 93.1427 | 15.8333 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108051020210 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16890C | SAMPFORD BRETT SAMPFORD BRETT SO | 102304 | SO on sewer network |  | Diluted | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | ST0903340211 | GB108051020250 | Doniford Stream | DONIFORD STREAM |  |  |  |  | Commissioned in 2018 - full year data expected | 32 | 15 | 22 | 40 | 265.9667 | 98.3113 | 24.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108051020250 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16891C | STOGUMBER STOGUMBER SO | 102305 | SO on sewer network |  | Diluted | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | ST0983437721 | GB108051020250 | Doniford Stream | TRIB OF DONIFORD STREAM |  |  |  |  | Mar 2023 |  |  |  | 10 | 5.4333 | 99.7549 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108051020250 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16893C | WILLITON UNION LANE SO | 102306 | SO on sewer network |  | Diluted | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | ST0817041740 | GB108051020250 | Doniford Stream | TRIB OF DONNIFORD STREAM (S) |  |  |  |  | Commissioned in 2019 - full year data expected | 16 | 11 | 11 | 19 | 18.4333 | 99.1027 | 12.8 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108051020250 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16896C | DILTON MARSH IN FIELD BEHIND 127 HIGH STREET | 101870 | SO on sewer network |  | Diluted | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8467049880 | GB109053021760 | Tributary - source to conf Biss Bk | TRIB OF ALLEBOURNE BROOK(S) |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 10 | 21 | 18.1 | 99.9992 | 15.5 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021760 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16898C | BRADFORD-ON-AVON SPRING FIELD AND WOOLLEY STREET JUNCTION | 101645 | SO on sewer network |  | Diluted | Rainwater | WEST WILTSHIRE | Chippenham Co Const | ST8290860796 | GB109053027372 | Bristol Avon (Semington Bk to By Bk) | RIVER AVON (VIA SWS) |  |  |  |  | Commissioned in 2018 - full year data expected | 23 | 18 | 14 | 28 | 63.8333 | 99.4517 | 13.625 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027372 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17027B | SOUTH CADBURY | 102161 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST6339025950 | GB108052015670 | Cam Tributary | TRIB OF RIVER CAM (S) |  |  |  |  | Aug 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015670 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17081B | SANDFORD ORCAS | 102523 | Inlet SO at WwTW |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | ST6181921542 | GB108052015620 | Corton Denham Stream | TRIBUTARY OF RIVER YEO |  |  |  |  | Commissioned in 2019 - full year data expected | 20 | 2 | 10 | 39 | 364.4667 | 100 | 17.2 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015620 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17179C | BRISTOL CROSSWAYS ROAD GARDEN R/O NO 114 | 011283 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST6027469895 | GB109053021980 | Brislington Bk - source to conf R Avon (Brist) | TRIB OF BRISLINGTON BROOK SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 100 | 0 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021980 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17268C | KINGSWOOD STATION ROAD | 103075 | SO on sewer network |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Filton and Bradley Stoke Co Const | ST6610075400 | GB109053027450 | Siston Bk - source to conf R Avon (Brist) | TRIB OF WARMLEY BROOK(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 24 | 19 | 13 | 32 | 136.3333 | 99.9962 | 22 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027450 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17273C | ALDERTON INLET | 103246 | Inlet SO at WwTW |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST8405083620 | GB109053027665 | Luckington Bk | TRIB OF LUCKINGTON BROOK(S) |  |  |  |  | Oct 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027665 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17286C | RADSTOCK WATERLOO ROAD/PINE COURT | 013132 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6950654966 | GB109053022271 | Wellow Bk - Snails Bk to Bristol Avon | WELLOW BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 25 | 13 | 19 | 26 | 74.8333 | 87.1773 | 20.75 | 5 (installed 2018) | Telemetry or data archiving failure / issue | Resolved - Oct | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022271 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17291B | CHARLTON MUSGROVE BARROW LANE | 401757 | Inlet SO at WwTW |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST7319031600 | GB108043015850 | Cale | TRIB OF RIVER CALE(S) |  |  |  |  | Aug 2023 |  |  |  | 59 | 1087.4122 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015850 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17504C | STREET FORD STREAM ROAD | 102380 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Wells Co Const | ST4717036630 | GB108052021181 | South Drain | BULLMEAD DITCH(S) |  |  |  |  | Commissioned in 2019 - full year data expected | 16 | 14 | 14 | 13 | 15.25 | 99.8916 | 14.25 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021181 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17549B | LOXTON SOUTH OF THE COACH HOUSE | NPSWQD008784 | Inlet SO at WwTW |  | Diluted | Rainwater | NORTH SOMERSET | Weston-Super-Mare Co Const | ST3772455518 | GB109052021580 | Lox Yeo - source to conf Rive Axe | AXE LINK RHTNE TO RIVER YEO |  |  |  |  | Jul 2023 |  |  |  | 1 | 4.55 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021580 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
18718B | CHAPMANSLADE DIVERS BRIDGE | 010613 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8269646992 | GB109053022110 | Rodden Bk - source to conf R Frome | RODDEN BROOK |  |  |  |  | Aug 2023 |  |  |  | 1 | 2.7619 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022110 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19121C | PORTISHEAD SLADE ROAD O/S 47 | 100558/CS/01 | SO on sewer network |  | Diluted | Rainwater | NORTH SOMERSET | North Somerset Co Const | ST4701076250 | GB109052027330 | Portbury Ditch - source to conf R Severn Estuary | TRIBUTARY OF PORTBURY DITCH |  |  |  |  | Commissioned in 2018 - full year data expected | 20 | 12 | 12 | 16 | 4.5333 | 99.9524 | 15 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052027330 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19171C | FILTON FILTON AVENUE R/G 699 | 010988 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Filton and Bradley Stoke Co Const | ST6145978870 | GB109053027540 | Stoke Bk - source to conf Bradley Bk | FILTON BROOK VIA SWS |  |  |  |  | Mar 2023 |  |  |  | 11 | 15.8333 | 99.7542 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027540 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19172C | FILTON CLEEVE RD MORTUARY | 101683 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Filton and Bradley Stoke Co Const | ST6074079980 | GB109053027540 | Stoke Bk - source to conf Bradley Bk | STOKE BROOK (S) |  |  |  |  | Oct 2023 | 9 | 9 | 3 | 10 | 3.9867 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027540 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19276C | TOCKINGTON MILL LODGE | 101957 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6050386197 | GB109054026650 | Chestle Pill | TOCKINGTON MILL RHINE |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 2 | 46 | 698.7333 | 99.7549 | 24 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026650 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19297C | WESTBURY FROGMORE ROAD OPP 67 | EPR/JB3891EW | SO on sewer network |  | Diluted | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8724751948 | GB109053021770 | Bitham Bk - source to conf Biss Bk | BITHAM BROOK/TRIB BITHAM BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 17 | 5 | 21 | 39 | 22.1 | 86.7557 | 16.4 | 5 (installed 2018) | Sensor failure / issue | Resolved - Aug |  |  |  | 2021-11-07 | Sewage litter present, no sewage fungus |  | N/A |  |  |  | Downstream assessment only | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021770 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19466C | GLASTONBURY MANOR HOUSE ROAD O/S TELEPHONE EXCHANGE | 102491 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Wells Co Const | ST4944439075 | GB108052021190 | Brue - Clyce Hole to conf North Drain | TRIB OF GLASTONBURY MILLSTREAM |  |  |  |  | Commissioned in 2020 - full year data expected |  | 21 | 13 | 22 | 14.1333 | 100 | 18.6667 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021190 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19582C | PORTISHEAD HIGH STREET NR BUILDERS YARD | Unpermitted | SO on sewer network |  | Diluted | Rainwater | NORTH SOMERSET | North Somerset Co Const | ST4700176244 | GB109052027330 | Portbury Ditch - source to conf R Severn Estuary | Portbury Ditch - source to conf R Severn Estuary |  |  |  |  | Dec 2023 |  |  |  | 3 | 0.46667 | 100 |  | <1 yr (installed 2023) | [5 empty] | 2020-05-05 | Sewage litter present, no sewage fungus | [6 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052027330 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19685B | HOLWELL NEW | 401159 | Inlet SO at WwTW |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | ST7110010790 | GB108043015960 | Caundle Brook (Lower) | THE CAUNDLE BROOK(S) |  |  |  |  | Oct 2023 |  |  |  | 40 | 636.1 | 99.8975 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015960 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19702C | BATH WELLSWAY JNC MILTON AVE | 103900 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7385064670 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | A CULVERTED TRIB OF RIVER AVON |  |  |  |  | Oct 2023 |  |  |  | 8 | 5 | 99.9962 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19731B | HARMANS CROSS TRANSFER STATION | 401237 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SY9911079940 | GB108044009920 | Swan (Swanage) | UNNAMED STREAM (S) |  |  |  |  | Jul 2023 |  |  |  | 13 | 65.5167 | 99.8653 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009920 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19778C | BRISTOL FISHPONDS STORM RETENTION TANK | 101280 | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol East Boro Const | ST6321075890 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | FISHPONDS BROOK VIA SWS |  |  |  |  | Jan 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19825C | TYTHERINGTON NEW HOUSE FARM DUCK ST | Unpermitted | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6727988090 | GB109053027590 | Laddon Bk - source to conf R Frome (Brist) | Laddon Bk - source to conf R Frome (Brist) |  |  |  |  | Mar 2023 |  |  |  | 15 | 185.4667 | 99.688 |  | <1 yr (installed 2023) | [5 empty] | 2023-01-27 | No sewage litter or sewage fungus | 2019-05-21 | Lab assessment - Impact |  |  |  | RICT unsuitable | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027590 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19904C | WICK SAINSBURY MILL | 102839 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6944772543 | GB109053027510 | Boyd - source to conf R Avon (Brist) | THE RIVER BOYD (S) |  |  |  |  | Jan 2023 |  |  |  | 10 | 78.35 | 99.8832 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027510 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19926C | BRISTOL MANOR WOOD OPEN SPACE RETENTION TANK | 101725 | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol South Boro Const | ST5733869246 | GB109053021970 | The Malago - source to conf R Avon (Brist New Cut) | THE MALAGO |  |  |  |  | Commissioned in 2018 - full year data expected | 23 | 9 | 16 | 27 | 63.1333 | 89.1202 | 15.375 | 5 (installed 2018) | Sensor failure / issue | Resolved - Aug | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021970 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19927C | BRISTOL HEADLEY ROAD ALLOTMENTS RETENTION TANK | 101822 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST5735068820 | GB109053021970 | The Malago - source to conf R Avon (Brist New Cut) | MALAGO (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 24 | 18 | 16 | 28 | 94.3333 | 99.9886 | 21.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021970 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19964C | BRISTOL HANHAM BRITANNIA ROAD TANK | 101761 | SO on sewer network |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6403073340 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | STRAD BROOK (S) |  |  |  |  | Commissioned in 2020 - full year data expected | 15 | 14 | 2 | 21 | 27.3333 | 98.0603 | 13 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19978B | ROOKSBRIDGE BRISTOL ROAD | 101956 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Wells Co Const | ST3690052340 | GB108052021250 | Mark Yeo | UNNAMED RHYNE(S) |  |  |  |  | Aug 2023 |  |  |  | 2 | 0.066667 | 99.933 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021250 | No |  |  | 2050 | Project to meet Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
12168C | RADSTOCK FROME ROAD | 013128 | SO on sewer network |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6921154871 | GB109053022271 | Wellow Bk - Snails Bk to Bristol Avon | WELLOW BROOK |  |  |  |  | Commissioned in 2020 - full year data expected |  | 1 | 0 | 1 | 0.75 | 99.9971 | 0.66667 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022271 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
12326B | NEW ROAD FERNDOWN | 401404 | Storm discharge at pumping station |  | Diluted | Rainwater | EAST DORSET | Christchurch Co Const | SZ0838099990 | GB108043011050 | Moors | TRIB OF MOORS RIVER(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 8 | 0 | 1 | 5 | 15 | 100 | 3.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011050 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
12772C | TROWBRIDGE WICKER HILL O/S MANE EVENT HAIRDRESSERS | EPRJB3891AZ | SO on sewer network |  | Diluted | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8536157988 | GB109053021791 | Biss (Bitham Bk to Bristol Avon) | RIVER BISS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 1 | 0.1 | 99.997 | 0.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021791 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
12773C | TROWBRIDGE ROSECROFT POLEBARN ROAD | EPRJB3891VH | SO on sewer network |  | Diluted | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8603857775 | GB109053021830 | Paxcroft Brook | PAXCROFT BROOK VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected |  | 14 | 0 | 1 | 0.2 | 99.9597 | 5 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021830 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13007C | ALVESTON LOWER HAZEL INLET | 010002 | Inlet SO at WwTW |  | Diluted | A combination of rainwater and groundwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6213287039 | GB109054026650 | Chestle Pill | TOCKINGTON MILL RHINE |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 4 | 36 | 124.8167 | 99.8967 | 20 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026650 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13008S | AMESBURY OFF CHURCH STREET STORM TANK | 401518 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SALISBURY | Salisbury Co Const | SU1516540808 | GB108043022352 | Hampshire Avon (Upper) d/s Nine Mile River confl | HAMPSHIRE AVON (S) |  |  |  |  | Commissioned in 2020 - full year data expected | 1 | 0 | 0 | 3 | 16.6333 | 99.9458 | 1 | 3 (installed 2020) | [12 empty] | Not RICT compliant | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022352 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13014B | AXBRIDGE OLD WRC SITE | 103918 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Wells Co Const | ST4299054090 | GB109052021540 | Cheddar Yeo - source to conf Stubbingham Rhyne | ELLENGE STREAM |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 99.5814 | 0 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021540 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13024S | BLACKHEATH STORM TANK | 042451 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | PURBECK | Mid Dorset and North Poole Co Const | SY9093392599 | GB108044010100 | Sherford River | SHERFORD RIVER |  |  |  |  | Commissioned in 2019 - full year data expected | 0 | 2 | 4 | 3 | 24.75 | 100 | 1.2857 | 4 (installed 2019) | [9 empty] | 2022-02-10 | Impact (US 0.34mg/l, DS 2.06mg/l) |  | Combined FE and SO | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010100 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13031C | BRADFORD-ON-AVON INLET PS INLET | 102190 | Inlet SO at WwTW |  | Diluted | Rainwater | WEST WILTSHIRE | Chippenham Co Const | ST8152060460 | GB109053027372 | Bristol Avon (Semington Bk to By Bk) | RIVER AVON |  |  |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 0 | 0 | 0 | 99.8992 | 0 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027372 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13047C | CANNINGTON INLET | 101442 | Inlet SO at WwTW |  | Diluted | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST2693039370 | GB108052021310 | Cannington Bk - Lower | CANNINGTON BROOK (S) |  |  |  |  | Commissioned in 2017 - full year data expected | 5 | 14 | 6 | 14 | 126.75 | 99.9092 | 7 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021310 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13054S | CHARFIELD STORM TANK | 102536 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST7202493205 | GB109054026600 | Little Avon - Ozleworth Bk to conf Tortworth Bk | LITTLE AVON |  |  |  |  | Commissioned in 2019 - full year data expected | 11 | 4 | 3 | 22 | 109.75 | 100 | 18.4 | 4 (installed 2019) | [5 empty] | 2023-05-03 | No sewage litter or sewage fungus | 2023-05-03 | TBC | 2022-05-27 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026600 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13061S | CHILCOMPTON STORM TANK | 102218 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | MENDIP | Wells Co Const | ST6512752900 | GB109053022251 | Somer | SOMER STREAM(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 9 | 5 | 4 | 27 | 230.75 | 99.9788 | 11.2 | 5 (installed 2018) | [5 empty] | 2021-05-14 | Sewage litter present, no sewage fungus | 2021-05-14 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022251 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13064C | CHIPPENHAM BLACKWELL HAMS INLET | 101637 | Inlet SO at WwTW |  | Diluted | A combination of rainwater and groundwater | NORTH WILTSHIRE | Chippenham Co Const | ST9176371284 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 3 | 1 | 1 | 0 | 0 | 99.4928 | 1.2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13070S | COLERNE STORM TANK | 102713 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST8316669867 | GB109053027380 | By Bk - conf Doncombe Bk to conf R Avon (Brist) | BY BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 5 | 2 | 2 | 11 | 45.5 | 99.9817 | 5 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027380 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13084C | CREWKERNE TRADING ESTATE CREWKERNE EAST INLET | 101456 | Inlet SO at WwTW |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST4508309655 | GB108052015260 | Parrett - headwaters to Broad River | CREWKERNE STREAM (S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 8 | 84 | 152.1553 | 98.6016 | 46 | 1 (installed 2022) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015260 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13087S | CROSCOMBE STORM TANK | 071798 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | MENDIP | Wells Co Const | ST5831444455 | GB108052021221 | Sheppey | RIVER SHEPPEY |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 99.8168 | 0 | 1 (installed 2022) | [5 empty] | 2021-03-19 | Sewage fungus present no sewage litter | [6 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021221 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13093B | DONIFORD | 101941 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | ST0874044010 | GB670807410000 | Bridgwater Bay | BRISTOL CHANNEL (C) |  | BLUE ANCHOR WEST | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=blue%20a&site=ukk2305-35200 |  | Commissioned in 2016 - full year data expected | 55 | 29 | 9 | 42 | 488.4171 | 99.9049 | 28.25 | 7 (installed 2016) |  |  | Performance - Infiltration | Scheduled | Stage 1b: Confirmed "asset maintenance" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB670807410000 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13096B | DORCHESTER LOUDS MILL ST GEORGES ROAD INLET | 401050 | Inlet SO at WwTW |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | SY7116090340 | GB108044009692 | Frome Dorset (Lower) d/s Louds Mill Dorchester | RIVER FROME(S) |  |  |  |  | Commissioned in 2021 - full year data expected |  | 0 | 3 | 18 | 165.7333 | 100 | 7 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009692 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13116S | ERLESTOKE ERLESTOKE PARK STORM TANK | 103629 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | KENNET | Devizes Co Const | ST9692054360 | GB109053022140 | Bulkington Drove w/c source to conf Semington Bk | ERLESTOKE STREAM(S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 3 | 8 | 18.75 | 99.8259 | 5.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022140 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13131C | FROME WELSHMILL LANE INLET | 102222 | Inlet SO at WwTW |  | Diluted | Rainwater | MENDIP | Somerton and Frome Co Const | ST7739048670 | GB109053022101 | Frome (Maiden Bradley to Mells) | RIVER FROME(S) |  |  |  |  | Commissioned in 2019 - full year data expected | 1 | 11 | 13 | 20 | 22.0344 | 100 | 9 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022101 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13153B | HOLTON HEATH HOLTON HEATH SEWAGE PUMPING STATION | 041577 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | Mid Dorset and North Poole Co Const | SY9517290626 | 68 | Not part of a river WB catchment | TRIB OF POOLE HARBOUR | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA | POOLE HARBOUR ROCKLEY SANDS | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=rockl&site=ukk2102-19450 |  | Commissioned in 2016 - full year data expected | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 7 (installed 2016) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13157C | HULLAVINGTON INLET | 101441 | Inlet SO at WwTW |  | Diluted | Groundwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST8962382856 | GB109053027730 | Gauze Bk - source to conf R Avon (Brist) | GAUZE BROOK (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027730 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13177S | LAVINGTON WOODBRIDGE STORM TANK | 101440 | Storm tank at WwTW |  | Diluted and partially treated | A combination of rainwater and groundwater | KENNET | Devizes Co Const | ST9984655078 | GB109053022130 | Semington Bk - source to conf Worton Str | SEMINGTON BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 12 | 3 | 13 | 24 | 139.0333 | 100 | 12.6667 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022130 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13198S | MARNHULL REED BEDS STORM TANK | 401339 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | NORTH DORSET | North Dorset Co Const | ST7933017540 | GB108043016051 | Stour (Middle u/s Pimperne Brook) | TRIB OF RIVER STOUR(S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 2 | 4 | 38.5608 | 99.992 | 3 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016051 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13200S | MARSHFIELD STORM TANK | 102728 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST7853173162 | GB109053027400 | Doncombe Bk - source to conf By Bk | DONCOMBE BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 8 | 9 | 8 | 18 | 74.25 | 100 | 10.2 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027400 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13222S | NORTH NIBLEY STORM TANK | 010063 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | STROUD | The Cotswolds Co Const | ST7316196858 | GB109054026630 | Doverte Brook | DOVERTE BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 2 | 15 | 7 | 31 | 322.6333 | 99.9148 | 11.2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026630 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13229S | OAKHILL STORM TANK | 011557 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | MENDIP | Wells Co Const | ST6504548352 | GB109053022020 | Mells source to conf with Somerset Frome | MELLS STREAM |  |  |  |  | Commissioned in 2019 - full year data expected | 2 | 3 | 3 | 21 | 237.7167 | 86.9258 | 6 | 4 (installed 2019) | Comms failure / issue | Scheduled | [7 empty] | 2022-03-21 | No impact (US 0.40mg/l, DS 0.31mg/l) |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022020 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13232S | PALMERSFORD STORM TANK | 401485 | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | CHRISTCHURCH | Christchurch Co Const | SZ1052097140 | GB108043011040 | Stour (Lower) | LOWER RIVER STOUR(S) |  | CHRISTCHURCH AVON BEACH/CHRISTCHURCH FRIAR'S CLIFF** | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=avon%20b&site=ukk2201-18800 | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=friar&site=ukk2201-18750 | Commissioned in 2016 - full year data expected | 4 | 0 | 0 | 23 | 242.1842 | 98.909 | 5.125 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011040 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13233C | PARBROOK INLET | 070086 | Inlet SO at WwTW |  | Diluted | Rainwater | MENDIP | Somerton and Frome Co Const | ST5665936603 | GB108052021130 | Coxbridge Brook( Brue) | TRIB OF COXBRIDGE BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 3 | 0 | 4 | 5 | 32.1333 | 99.9973 | 3 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021130 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13242B | POOLE CABOT LANE INLET PS | 401354 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | POOLE | Poole Boro Const | SZ0071093560 | GB520804415800 | POOLE HARBOUR | TRIBUTARY OF HOLES BAY(E) | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA | POOLE HARBOUR HAMWORTH PARK /POOLE HARBOUR ROCKLEY SANDS / POOLE HARBOUR LAKE | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=rockl&site=ukk2102-19450 | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=harbour%20lake&site=ukk2102-19400 | Commissioned in 2016 - full year data expected | 3 | 3 | 0 | 0 | 0 | 100 | 1.5 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB520804415800 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13249S | PUDDLETOWN PIDDLEHINTON ROAD | Unpermitted | Storm tank at WwTW |  | Diluted and partially treated | Groundwater | WEST DORSET | West Dorset Co Const | SY7506394925 | GB108044010120 | Piddle (Upper) | Piddle (Upper) |  |  |  |  | Commissioned in 2021 - full year data expected |  |  |  | 0 | 0 | 100 | 0 | 2 (installed 2021) | [5 empty] | 2023-10-25 | No sewage litter or sewage fungus | 2023-10-25 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010120 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13253S | RATFYN STORM TANK | 401500 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SALISBURY | Salisbury Co Const | SU1559042730 | GB108043022352 | Hampshire Avon (Upper) d/s Nine Mile River confl | HAMPSHIRE AVON RIVER |  |  |  |  | Commissioned in 2020 - full year data expected |  | 0 | 0 | 0 | 0 | 100 | 0 | 3 (installed 2020) | [5 empty] | 2021-05-04 | No sewage litter or sewage fungus | [5 empty] | Not RICT compliant | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022352 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13254S | REDWICK STORM TANK | 103775 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Filton and Bradley Stoke Co Const | ST5469086260 | GB109054026650 | Chestle Pill | THE CHESTLE PILL RIVER |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 4 | 23 | 284.7167 | 99.9206 | 13.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026650 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13257S | ROWDE STORM TANK | 101462 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | KENNET | Devizes Co Const | ST9679462749 | GB109053022220 | Summerham Brook | SUMMERHAM BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 6 | 3 | 0 | 8 | 73.2667 | 99.7979 | 3.6 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022220 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13288S | STOGURSEY STORM TANK | 101438 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | ST2046843363 | GB108052021340 | Stogursey BK | STOGURSEY BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 0 | 10 | 13 | 49 | 426 | 99.8771 | 15.2 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021340 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13293S | STRATTON ON THE FOSSE STORM TANK | 011558 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | MENDIP | Somerton and Frome Co Const | ST6634050900 | GB109053022240 | Snails Bk - source to conf Kilmersdon Str | LUCCOMBE WATERCOURSE (S) |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 1 | 6 | 73.95 | 99.9964 | 3.5 | 2 (installed 2021) | [9 empty] | 2022-03-21 | Impact (US 0.36 mg/l, DS 0.45mg/l) |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022240 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13308C | THINGLEY COPPERSHELL LANE INLET | 102328 | Inlet SO at WwTW |  | Diluted | A combination of rainwater and groundwater | NORTH WILTSHIRE | Chippenham Co Const | ST9190067590 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | BYDE MILL BROOK/RIVER AVON |  |  |  |  | Commissioned in 2019 - full year data expected | 5 | 3 | 2 | 7 | 3.5667 | 100 | 3.4 | 4 (installed 2019) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13322S | URCHFONT STORM TANK | 101668 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | KENNET | Devizes Co Const | SU0393557519 | GB109053022210 | Worton Str - source to conf Semington Bk | SEMINGTON BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 8 | 6 | 7 | 16 | 117.7 | 99.6689 | 9.2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022210 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13332S | WELLS STORM TANK | 101432 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | MENDIP | Wells Co Const | ST5335344859 | GB108052021240 | Keward Brook | WELLS MOAT STREAM(S) |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 9 | 35 | 253.6 | 98.9311 | 22 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021240 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13337B | WEST LULWORTH HAMBURY FARM | 401815 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SY8242079730 | GB620705550000 | Dorset / Hampshire | ENGLISH CHANNEL(C) |  | LULWORTH COVE | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=lulw&site=ukk2204-20000 |  | Commissioned in 2016 - full year data expected | 10 | 5 | 2 | 8 | 21.8636 | 99.9936 | 6.25 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620705550000 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13338B | WESTBURY INLET | 101652 | Inlet SO at WwTW |  | Diluted | A combination of rainwater and groundwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8717252598 | GB109053021770 | Bitham Bk - source to conf Biss Bk | BITHAM BROOK/TRIB BITHAM BROOK |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 1 | 6 | 10.7667 | 99.9909 | 3.5 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021770 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13351C | WINSCOMBE INLET | 071977 | Inlet SO at WwTW |  | Diluted | A combination of rainwater and groundwater | NORTH SOMERSET | Weston-Super-Mare Co Const | ST3999157769 | GB109052021580 | Lox Yeo - source to conf Rive Axe | LOX YEO RIVER |  |  |  |  | Commissioned in 2021 - full year data expected |  | 0 | 2 | 4 | 24.2669 | 99.9584 | 2 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021580 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13354C | WIVELISCOMBE HILLSMOOR INLET | NPSWQD000307 | Inlet SO at WwTW |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST0857727376 | GB108052015510 | Hillfarrance Bk | TRIB OF HILLFARRANCE BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 9 | 11 | 8 | 8 | 4 | 99.9092 | 9 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015510 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13373B | PORLOCK WEIR | 100353 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | SS8671048040 | GB610807680004 | Bristol Channel Outer South | PORLOCK BAY(C) |  | PORLOCK WEIR | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=porlo&site=ukk2305-34900 |  | Commissioned in 2016 - full year data expected | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB610807680004 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13381B | WEST MILTON INLET | 041658 | Inlet SO at WwTW |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | SY4989696271 | GB108044009590 | Mangerton Brook | TRIB OF MANGERTON RIVER |  |  |  |  | Commissioned in 2018 - full year data expected | 16 | 5 | 7 | 19 | 76.3333 | 99.9087 | 11.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009590 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13389B | BOSSINGTON | 100138 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | SS8910048500 | GB610807680004 | Bristol Channel Outer South | PORLOCK BAY(C) |  |  |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 0 | 0 | 0 | 99.9907 | 4.2 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB610807680004 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
13917C | BOURNEMOUTH SEAMOOR ROAD O/S 73A | Unpermitted | SO on sewer network |  | Diluted | Rainwater | BOURNEMOUTH | Bournemouth West Boro Const | SZ0797589819 | GB620705550000 | Dorset / Hampshire | Dorset / Hampshire |  |  |  |  | Sep 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620705550000 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14002B | BATH MIDLAND ROAD TWERTON | 102287 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7390065092 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2019 - full year data expected | 3 | 3 | 0 | 0 | 0 | 100 | 2.8 | 4 (installed 2019) | [9 empty] | 2021-10-25 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14046B | PEWSEY SWAN | 401642 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | KENNET | Devizes Co Const | SU1645059730 | GB108043022410 | Hampshire Avon (East) and Woodborough Stream | RIVER AVON (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 9 | 2 | 4 | 1.5494 | 100 | 3.75 | 5 (installed 2018) | [5 empty] | 2023-05-17 | No sewage litter or sewage fungus | 2023-05-17 | TBC | 2021-10-18 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022410 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14049B | PEWSEY WILCOT LODGE | NPSWQD003670 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | KENNET | Devizes Co Const | SU1414060710 | GB108043022410 | Hampshire Avon (East) and Woodborough Stream | TRIBUTARY OF THE RIVER AVON |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 2 | 6 | 27.3833 | 99.9622 | 4 | 1 (installed 2022) | [9 empty] | 2021-10-18 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022410 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14055B | MARDEN HIGH STREET | 402523 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | KENNET | Devizes Co Const | SU0865957654 | GB108043022370 | Hampshire Avon (West) | TRIBUTARY OF THE RIVER AVON |  |  |  |  | Commissioned in 2020 - full year data expected |  | 0 | 0 | 6 | 49.45 | 99.8548 | 2 | 3 (installed 2020) | [9 empty] | 2021-10-18 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022370 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14064B | KINGSWOOD WILLSBRIDGE | NPSWQD001439 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6648970433 | GB109053027450 | Siston Bk - source to conf R Avon (Brist) | SISTON BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 2 | 0.66667 | 99.089 | 2.1667 | 5 (installed 2018) | [9 empty] | 2021-10-25 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027450 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14069B | STREET HOUNDWOOD DROVE | 103572 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Wells Co Const | ST4718036840 | GB108052021181 | South Drain | TRIB OF THE BULLMEAD DITCH |  |  |  |  | Commissioned in 2018 - full year data expected | 5 | 7 | 4 | 4 | 26.25 | 99.9344 | 4.2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021181 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14074B | SHEPTON MALLET FOSSE LANE CHARLTON | 103573 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Wells Co Const | ST6286843412 | GB108052021221 | Sheppey | RIVER SHEPPEY VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected |  | 0 | 1 | 2 | 0.31667 | 100 | 1 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021221 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14076B | EVERCREECH STONEY STRATTON | 103622 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Somerton and Frome Co Const | ST6557738981 | GB108052021160 | Alham | TRIBUTARY OF RIVER ALHAM |  |  |  |  | Commissioned in 2019 - full year data expected | 8 | 1 | 2 | 2 | 4.0833 | 100 | 3.25 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021160 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14084B | GLASTONBURY ACTIS | 102497 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Wells Co Const | ST5045037840 | GB108052021130 | Coxbridge Brook( Brue) | TRIBUTARY OF RIVER BRUE (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 11 | 6 | 5 | 4 | 19.1333 | 95.7032 | 8.8 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021130 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14085B | COXLEY COXLEY RIPPLE | 102367 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Wells Co Const | ST5233443283 | GB108052021221 | Sheppey | TRIB OF RIVER SHEPPEY |  |  |  |  | Commissioned in 2020 - full year data expected |  | 6 | 2 | 8 | 71.4833 | 99.973 | 5.3333 | 3 (installed 2020) | [9 empty] | 2022-01-14 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021221 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14092B | GLASTONBURY WELLS ROAD | 102377 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Wells Co Const | ST5066040300 | GB108052021171 | Hartlake | TRIB OF RIVR SHEPPEY(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 6 | 7 | 7 | 10 | 45.15 | 99.9799 | 6.2 | 5 (installed 2018) | [9 empty] | 2022-01-14 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021171 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14093B | WEST PENNARD PAGE LANE | 103782 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Somerton and Frome Co Const | ST5495938813 | GB108052021171 | Hartlake | TRIBUTARY OF TEN FOOT RHYNE |  |  |  |  | Commissioned in 2020 - full year data expected |  | 0 | 0 | 2 | 13.35 | 100 | 0.66667 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021171 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14097B | BALTONSBOROUGH BALTONSBOROUGH MAIN 2 | 103055 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Somerton and Frome Co Const | ST5433034790 | GB108052021182 | Brue - Tootle Bridge to Clyse Hole | THE MILL STREAM(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 3 | 5 | 2 | 1 | 8 | 100 | 2.2 | 5 (installed 2018) | [9 empty] | 2022-05-05 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021182 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14099B | STREET WALTON GLOBE | 103783 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Wells Co Const | ST4551036510 | GB108052021181 | South Drain | A TRIB OF THE SMALL MOOR RHYNE |  |  |  |  | Commissioned in 2020 - full year data expected |  | 1 | 0 | 0 | 0 | 100 | 0.33333 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021181 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14108B | MELLS | 102696 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Somerton and Frome Co Const | ST7303048980 | GB109053022020 | Mells source to conf with Somerset Frome | MELLS STREAM(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 5 | 3 | 0 | 3 | 11 | 99.9715 | 2.4 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022020 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14120B | STREET MIDDLE BROOKS ROAD | 100744 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Wells Co Const | ST4772035272 | GB108052021181 | South Drain | (S) TRIB OF BULLMEAD DITCH |  |  |  |  | Commissioned in 2020 - full year data expected |  | 3 | 4 | 9 | 81.75 | 99.9182 | 5.3333 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021181 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14127B | GILLINGHAM BRICKYARD LANE | 401128 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH DORSET | North Dorset Co Const | ST8064125899 | GB108043022490 | Stour (Headwaters) | RIVER STOUR |  |  |  |  | Commissioned in 2020 - full year data expected |  | 0 | 0 | 0 | 0 | 100 | 0 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022490 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14132C | BRANSGORE WILTSHIRE GARDENS | 401565 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | CHRISTCHURCH | Christchurch Co Const | SZ1777097800 | GB108043011011 | Clockhouse Stream | CLOCKHOUSE STREAM(S) |  |  |  |  | Commissioned in 2019 - full year data expected | 4 | 3 | 1 | 15 | 33.3444 | 99.7222 | 5.75 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011011 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14147B | CHIPPENHAM WESTMEAD | 100823 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | Chippenham Co Const | ST9201872133 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | RIVER AVON |  |  |  |  | Commissioned in 2019 - full year data expected | 5 | 1 | 4 | 21 | 300.35 | 99.93 | 7.75 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14158B | HULLAVINGTON RAF STATION | 101678 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9071080390 | GB109053027720 | Rodbourne Bk - source to conf R Avon (Brist) | TRIB RIVER AVON (S) |  |  |  |  | Commissioned in 2020 - full year data expected | 5 | 3 | 2 | 12 | 134.5 | 93.2021 | 5.5 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027720 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14162B | MALMESBURY BURTON HILL | 103660 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9323086500 | GB109053027690 | Sherston Avon | TRIB OF RIVER AVON(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 3 | 2 | 3 | 4 | 10.7667 | 99.7812 | 2.6667 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027690 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14196B | MALMESBURY NOAHS ARK | 101696 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9595088570 | GB109053027770 | Charlton Str - source to conf Bristol Avon | TRIB RIVER AVON (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 4 | 1 | 3 | 50 | 718.0347 | 100 | 14.2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027770 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14221C | UPTON FRENCHS FARM | JB3793WZ | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | Mid Dorset and North Poole Co Const | SY9684693154 | GB108044010100 | Sherford River | TRIB OF SHERFORD RIVER |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 1 | 6 | 23.4667 | 99.8946 | 3.5 | 1 (installed 2022) | [5 empty] | 2020-10-26 | No sewage litter or sewage fungus | 2021-03-15 | Lab assessment - No impact |  |  |  | RICT analysis complete (Impact high) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010100 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14226B | CHURCH KNOWLE GLEBE FARM | 401417 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SY9506581663 | GB108044010020 | Corfe River | TRIBUTARY OF CORFE RIVER |  |  |  |  | Commissioned in 2020 - full year data expected |  | 11 | 6 | 34 | 200.1667 | 100 | 17 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010020 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14229B | WAREHAM WEST MILL CRESCENT | 401202 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | PURBECK | Mid Dorset and North Poole Co Const | SY9161687923 | GB108044010080 | Piddle (Lower) | TRIB OF RIVER PIDDLE | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA |  |  |  | Commissioned in 2016 - full year data expected | 10 | 1 | 0 | 0 | 0 | 100 | 3.25 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010080 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14232B | CHURCH KNOWLE ANIMAL SANCTUARY | 401419 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SY9376781585 | GB108044010020 | Corfe River | A TRIBUTARY OF THE CORFE RIVER |  |  |  |  | Commissioned in 2020 - full year data expected | 11 | 9 | 5 | 27 | 114.4919 | 99.9997 | 13 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010020 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14243B | MORDEN COCK AND BOTTLE | 401197 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | Mid Dorset and North Poole Co Const | SY9135494678 | GB108044010100 | Sherford River | TRIB OF SHERFORD RIVER |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 2 | 10.9189 | 98.717 | 0.5 | 5 (installed 2018) | [9 empty] | 2022-02-10 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010100 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14248B | EAST BURTON CROSS ROADS | 401422 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SY8316686975 | GB108044009650 | Frome Dorset Trib (River Win) | RIVER WIN |  |  |  |  | Commissioned in 2019 - full year data expected | 12 | 1 | 0 | 2 | 13.3833 | 100 | 3.2 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009650 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14255B | STOBOROUGH RIDGE | 401423 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SY9376086635 | 68 | Not part of a river WB catchment | TRIBUTARY OF RIVER FROME | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA |  |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 1 | 10 | 60.55 | 99.9584 | 1.375 | 7 (installed 2016) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14256B | AFFPUDDLE | 401424 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SY8060793678 | GB108044010080 | Piddle (Lower) | TRIBUTARY OF RIVER PIDDLE |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 5 (installed 2018) | [9 empty] | 2021-10-13 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010080 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14259B | WAREHAM SOUTH EAST | 402472 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | Mid Dorset and North Poole Co Const | SY9267087240 | 68 | Not part of a river WB catchment | RIVER FROME (ESTUARINE) | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA |  |  |  | Commissioned in 2016 - full year data expected | 7 | 6 | 4 | 11 | 24.5 | 99.9783 | 5.625 | 7 (installed 2016) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14264B | EAST KNIGHTON | 401425 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SY8140085590 | GB108044009650 | Frome Dorset Trib (River Win) | TRIBUTARY OF RIVER WIN |  |  |  |  | Commissioned in 2020 - full year data expected |  | 1 | 0 | 0 | 0 | 100 | 0.33333 | 3 (installed 2020) | [9 empty] | 2021-10-13 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009650 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14266B | WAREHAM SANDFORD LANE | 401201 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | Mid Dorset and North Poole Co Const | SY9209988177 | GB108044010080 | Piddle (Lower) | TRIB OF RIVER PIDDLE(S) | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA |  |  |  | Commissioned in 2016 - full year data expected | 0 | 1 | 0 | 0 | 0 | 97.8721 | 0.125 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010080 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14374B | HIGHBRIDGE NEWTON INLET | 102480 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Wells Co Const | ST3115047340 | GB540805210900 | PARRETT | RIVER BRUE (E) |  | BURNHAM JETTY NORTH | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=burnh&site=ukk2302-35300 |  | Commissioned in 2016 - full year data expected | 0 | 0 | 0 | 9 | 12.25 | 99.131 | 1.5 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB540805210900 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14270B | BOVINGTON TERMINAL | 401426 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SY8345888000 | GB108044009692 | Frome Dorset (Lower) d/s Louds Mill Dorchester | A TRIBUTARY OF THE RIVER FROME |  |  |  |  | Commissioned in 2021 - full year data expected |  | 0 | 0 | 3 | 12.9167 | 99.9968 | 1 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009692 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14274B | EAST CHALDON | 401427 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SY7948083470 | GB108044009650 | Frome Dorset Trib (River Win) | A TRIBUTARY OF THE RIVER WIN |  |  |  |  | Commissioned in 2020 - full year data expected |  | 3 | 2 | 12 | 89 | 100 | 5.6667 | 3 (installed 2020) | [9 empty] | 2021-10-13 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009650 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14275B | CORFE CASTLE HALVES COTTAGES | 401428 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SY9620181348 | GB108044010020 | Corfe River | A TRIBUTARY OF THE CORFE RIVER |  |  |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 0 | 0 | 96.0806 | 0 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010020 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14289B | ILCHESTER ILCHESTER MAIN | 012884 | Storm discharge at pumping station |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5215122880 | GB108052015682 | Yeo Ds Over Compton | RIVER YEO |  |  |  |  | Commissioned in 2018 - full year data expected | 1 | 1 | 1 | 5 | 34.7167 | 99.999 | 2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015682 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14293B | QUEEN CAMEL ENGLANDS MEAD GREEN LANE | 071692 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST5929524947 | GB108052015650 | Cam - Lower | RIVER CAM |  |  |  |  | Commissioned in 2018 - full year data expected | 1 | 0 | 0 | 5 | 29.6667 | 100 | 1.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015650 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14294B | DONYATT | 102568 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST3398614019 | GB108052015190 | Isle - Upper to conf Cad Bk | RIVER ISLE |  |  |  |  | Commissioned in 2018 - full year data expected | 4 | 8 | 2 | 16 | 94 | 99.9543 | 6.6 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015190 | Yes |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14295B | YEOVILTON WEIR | 101765 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5452022700 | GB108052015682 | Yeo Ds Over Compton | RIVER YEO (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 7 | 82.9667 | 91.3118 | 1.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015682 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14323B | AMESBURY FLOWER LANE | 401046 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SALISBURY | Salisbury Co Const | SU1537941184 | GB108043022352 | Hampshire Avon (Upper) d/s Nine Mile River confl | RIVER AVON |  |  |  |  | Commissioned in 2020 - full year data expected | 1 | 0 | 0 | 0 | 0 | 100 | 0.25 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022352 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14378B | BRIDGWATER BLAKE GARDENS | 102691 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3018036790 | GB540805210900 | Parrett | RIVER PARRETT(TIDAL)(E) |  | BURNHAM JETTY NORTH | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=burnh&site=ukk2302-35300 |  | Commissioned in 2016 - full year data expected | 0 | 0 | 2 | 0 | 0 | 100 | 0.25 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB540805210900 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14380B | NORTH NEWTON CHURCH ROAD | 101802 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3022031100 | GB108052021360 | Petherton Stream | TRIB OF RIVER TONE (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 4 | 3 | 0 | 1 | 5.5 | 94.2935 | 2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021360 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14385B | BRIDGWATER BRISTOL ROAD | 082162 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3063038490 | 200 | Not part of a river WB catchment | TRIB OF RIVER PARRETT |  | BURNHAM JETTY NORTH | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=burnh&site=ukk2302-35300 |  | Commissioned in 2016 - full year data expected | 8 | 10 | 17 | 12 | 23.41 | 100 | 11.125 | 7 (installed 2016) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14386B | GREINTON MOOR DRIVE | 102299 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST4122136246 | GB108052021150 | King's Sedgemoor Drain - Henley Sluice to mouth | TRIB GREINTON RHYNE DRAIN (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 2 | 7 | 5 | 4 | 12.5167 | 99.9921 | 4.5 | 5 (installed 2018) | [9 empty] | 2022-03-01 | No impact (US 1.24mg/l, DS 1.01mg/l) |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021150 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14388B | BERKELEY PARK VIEW ROAD | 103822 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | STROUD | Stroud Co Const | ST6790099170 | GB109054026630 | Doverte Brook | THE BERKELEY PILL |  |  |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 0 | 0 | 0 | 100 | 0.5 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026630 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14391B | STOKE ST GREGORY NO 1 LANE END | 101803 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST3410027190 | GB108052015450 | West Sedgemoor Main Drain | STORM CULVERT (S) |  |  |  |  | Commissioned in 2019 - full year data expected | 1 | 0 | 0 | 2 | 7 | 99.9848 | 0.75 | 4 (installed 2019) | [9 empty] | 2022-01-17 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015450 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14405B | WEST STAFFORD DORCHESTER ROAD | 401967 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | SY7250689763 | GB108044010060 | South Winterbourne | SOUTH WINTERBOURNE |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 0 | 1 | 6.1667 | 100 | 0.5 | 2 (installed 2021) | [12 empty] | Study in 2021 to assess the impact of Amesbury and Ratfyn WRCs. No separation of settled storm overflow and treated final effluent at Ratfyn. An impact from the outfall was detected though apparent recovery within 1km. No sign of sewage litter. | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010060 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14410B | BURTON BRADSTOCK BURTON SOUTHOVER | 401968 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | SY4849089360 | GB108044009550 | Bride | RIVER BRIDE (S) |  | HIVE (BURTON BRADSTOCK) | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=hive&site=ukk2205-20970 |  | Commissioned in 2016 - full year data expected | 2 | 2 | 0 | 3 | 21.1 | 99.784 | 2.75 | 7 (installed 2016) | [9 empty] | 2021-10-14 | Inaccessible at time of visit |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009550 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14420B | MINEHEAD QUAY WEST | 101776 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | SS9710047380 | GB640807670000 | Bristol Channel Inner South | BRISTOL CHANNEL(C) |  | MINEHEAD TERMINUS | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=mineh&site=ukk2305-35000 |  | Commissioned in 2016 - full year data expected | 1 | 0 | 0 | 1 | 0.75 | 100 | 0.375 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB640807670000 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14423B | BLUE ANCHOR PILL BRIDGE | 102437 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | ST0273043490 | GB108051020390 | Pill | RIVER PILL (F) |  | BLUE ANCHOR WEST | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=blue%20a&site=ukk2305-35200 |  | Commissioned in 2016 - full year data expected | 1 | 0 | 0 | 19 | 144.7667 | 99.9848 | 2.625 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108051020390 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14440B | DILTON MARSH PEN KNAPP | 103205 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8585049850 | GB109053021750 | Biss Bk - source to conf unnamed trib | BISS BROOK(S) |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 0 | 1 | 1.9667 | 99.9905 | 0.5 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021750 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14447B | KEEVIL THE STREET | 011447 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST9235058210 | GB109053022150 | MIlebourne Str - source to conf Semington Bk | TRIB OF SEMINGTON BROOK (S) |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 2 | 7 | 66.8 | 99.9713 | 4.5 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022150 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14452B | FRESHFORD NEW INN | 103786 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST7909259965 | GB109053021840 | Somerset Frome conf with Mells to conf B. Avo | RIVER FROME |  |  |  |  | Commissioned in 2019 - full year data expected | 8 | 2 | 5 | 9 | 4.4167 | 99.9876 | 6 | 4 (installed 2019) | [9 empty] | 2023-01-03 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14458B | NORTH BRADLEY CHURCHLANDS | 103244 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8568854762 | GB109053021750 | Biss Bk - source to conf unnamed trib | TRIBUTARY OF BISS BROOK(S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 100 | 0 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021750 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14459B | SOUTHWICK CHANTRY GARDENS | 021630 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8418755339 | GB109053021800 | Lambrok Str - source to conf R Biss | LAMBROK STREAM |  |  |  |  | Commissioned in 2020 - full year data expected | 11 | 4 | 9 | 17 | 115.5525 | 99.9971 | 10.25 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021800 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14462B | BROUGHTON GIFFORD CURTIS ORCHARD | 100633 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | Chippenham Co Const | ST8804463526 | GB109053021890 | Chalfield Brook - source to conf Avon | TRIB. OF CHALFIELD BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 5 | 11 | 79.6667 | 99.9985 | 8 | 1 (installed 2022) | [9 empty] | 2022-04-14 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021890 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14469B | GREAT HINTON | NPSWQD008924 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST9091459220 | GB109053022200 | Semington Bk-Milebourne Str to conf R Avon (Brist) | TRIBUTARY OF SEMINGTON BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 8 | 0 | 3 | 13 | 84.6667 | 57.398 | 6 | 4 (installed 2019) | Comms failure / issue | Resolved - Sep | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022200 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14502B | BRISTOL WHITBY ROAD B CO-OP DEPOT ARNOS VALE | 021674 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol East Boro Const | ST6117671958 | 157 | Not part of a river WB catchment | RIVER AVON (ESTUARINE) |  |  |  |  | Commissioned in 2017 - full year data expected | 0 | 4 | 3 | 2 | 5.5667 | 100 | 1.2857 | 6 (installed 2017) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14507B | SHIREHAMPTON LAMPLIGHTERS | 011540 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol North West Boro Const | ST5263076270 | 158 | Not part of a river WB catchment | TRIB OF RIVER AVON (S) |  |  |  |  | Commissioned in 2020 - full year data expected | 6 | 1 | 3 | 1 | 0.2 | 99.8992 | 2.75 | 3 (installed 2020) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14550B | LACOCK NETHERCOTE HILL | 010701 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | Chippenham Co Const | ST9176168698 | GB109053021960 | Bydemill Bk - source to conf RIver Avon (Brist) | BYDE MILL BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 9 | 6 | 5 | 12 | 55.5833 | 99.9765 | 7.2 | 4 (installed 2019) | [9 empty] | 2023-01-10 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021960 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14562B | GLASTONBURY WIRRAL PARK | 103823 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Wells Co Const | ST4909238795 | GB108052021190 | Brue - Clyce Hole to conf North Drain | GLASTONBURY MILL STREAM |  |  |  |  | Commissioned in 2020 - full year data expected |  | 0 | 0 | 0 | 0 | 99.9996 | 0 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021190 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14563B | FROME COURTS BARTON MARSTON LANE | 102701 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | MENDIP | Somerton and Frome Co Const | ST7637846582 | GB109053022000 | Nunney Bk - source to conf Mells R | TRIBUTARY OF NUNNEY BROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 0 | 0 | 0 | 99.9077 | 0 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022000 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14581B | BRISTOL VICTORIA ROAD | 012020 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol North West Boro Const | ST5167077470 | 158 | Not part of a river WB catchment | BRISTOL AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 2 | 1 | 0 | 0 | 0 | 100 | 0.75 | 5 (installed 2018) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14621B | PORTISHEAD TOWN HARBOUR ROAD | 070308 | Storm discharge at pumping station |  | Diluted | Groundwater | NORTH SOMERSET | North Somerset Co Const | ST4762076400 | GB109052027330 | Portbury Ditch - source to conf R Severn Estuary | PORTBURY DITCH,TRIB |  |  |  |  | Commissioned in 2017 - full year data expected | 5 | 0 | 0 | 12 | 61.4167 | 99.9332 | 4.25 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052027330 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14624B | SALTFORD MEAD LANE | 011904 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6884267539 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 4 | 2 | 0 | 10 | 101.4658 | 99.8742 | 3.2 | 4 (installed 2019) | [9 empty] | 2021-12-10 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14632B | TAUNTON MAIDENBROOK | 070804 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST2452025700 | GB108052015482 | Tone Ds Taunton | RIVER TONE |  |  |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015482 | Yes |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15042B | BURTON STONY LANE | 402473 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | CHRISTCHURCH | Christchurch Co Const | SZ1611094770 | GB108043011011 | Clockhouse Stream | THE CLOCKHOUSE STREAM |  |  |  |  | Commissioned in 2020 - full year data expected |  | 0 | 0 | 1 | 0.23333 | 69.1707 | 0.33333 | 3 (installed 2020) | Telemetry or data archiving failure / issue | Resolved - Nov | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011011 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15043B | MUDEFORD GARDENS | 401748 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | CHRISTCHURCH | Christchurch Co Const | SZ1821092140 | GB108043011020 | Mude | RIVER MUDE(S) |  | CHRISTCHURCH AVON BEACH/CHRISTCHURCH FRIAR'S CLIFF | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=avon%20b&site=ukk2201-18800 | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=friar&site=ukk2201-18750 | Commissioned in 2016 - full year data expected | 0 | 0 | 0 | 0 | 0 | 98.3914 | 0.375 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011020 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15047B | FERNDOWN REDWOOD DRIVE | 400647 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | EAST DORSET | Christchurch Co Const | SU0737001820 | GB108043011080 | Uddens Water | TRIBUTARY OF UDDENS WATER |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 99.6766 | 0.2 | 5 (installed 2018) | [7 empty] | 2020-05-01 | Lab assessment - No impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011080 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15048B | VERWOOD ACACIA AVENUE | 400642 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | EAST DORSET | North Dorset Co Const | SU1014407666 | GB108043016090 | Crane (Dorset) | TRIB. EBBLAKE STREAM VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected |  | 1 | 0 | 0 | 0 | 79.4678 | 0.33333 | 3 (installed 2020) | Telemetry or data archiving failure / issue | Scheduled | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016090 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15057B | FERNDOWN THAMES CLOSE | 401154 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | EAST DORSET | Christchurch Co Const | SU0943001130 | GB108043011050 | Moors | TRIB OF MOORS RIVER (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 1 | 2 | 3 | 0 | 0 | 99.7546 | 1.5 | 5 (installed 2018) | [7 empty] | 2016-08-22 | Lab assessment - Impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011050 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15060B | WEST MOORS PENNINGTON COPSE | 400645 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | EAST DORSET | Christchurch Co Const | SU0777402370 | GB108043011080 | Uddens Water | TRIB OF UDDENS WATER |  |  |  |  | Commissioned in 2017 - full year data expected | 7 | 1 | 0 | 10 | 80.1667 | 100 | 3.3333 | 6 (installed 2017) | [7 empty] | 2020-05-01 | Lab assessment - No impact |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011080 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15068B | ST LEONARDS WAYSIDE ROAD NO 1 | 402453 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | EAST DORSET | Christchurch Co Const | SU1096802199 | GB108043011050 | Moors | TRIBUTARY OF MOORS RIVER |  |  |  |  | Commissioned in 2018 - full year data expected | 1 | 3 | 0 | 11 | 50.5 | 99.871 | 3.2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011050 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15070B | WIMBORNE HAYES LANE COLEHILL | 401780 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | EAST DORSET | Christchurch Co Const | SZ0348599849 | GB108043011040 | Stour (Lower) | TRIB OF RIVER STOUR |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 6 | 5 | 24.75 | 98.0793 | 5.5 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011040 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15078B | FERNDOWN A31 TRICKETTS CROSS | 401156 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | EAST DORSET | Christchurch Co Const | SU0912601456 | GB108043011080 | Uddens Water | UDDENS WATER |  |  |  |  | Commissioned in 2017 - full year data expected | 5 | 8 | 0 | 5 | 28.5667 | 98.0582 | 3.3333 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011080 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15079B | WIMBORNE POOLE ROAD | 401624 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | EAST DORSET | Mid Dorset and North Poole Co Const | SZ0147099390 | GB108043011040 | Stour (Lower) | RIVER ALLEN (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 1 | 0 | 0 | 0 | 100 | 0.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011040 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15080B | FERNDOWN DUGDELL CLOSE | 400649 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | EAST DORSET | Christchurch Co Const | SU0887700616 | GB108043011050 | Moors | TRIB OF MOORS RIVER |  |  |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011050 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15083B | ST LEONARDS FOREST EDGE DRIVE | 402454 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | EAST DORSET | Christchurch Co Const | SU1086204683 | GB108043016090 | Crane (Dorset) | TRIB. THE MOORS RIVER VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 2 | 17 | 94 | 93.6769 | 9.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016090 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15090B | WEST PARLEY CHURCH LANE | 401157 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | EAST DORSET | Christchurch Co Const | SZ0842296933 | GB108043011040 | Stour (Lower) | RIVER STOUR |  |  |  |  | Commissioned in 2021 - full year data expected | 23 | 10 | 16 | 30 | 236.4333 | 99.9996 | 17.1667 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011040 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15091B | FERNDOWN ALDRIDGE ROAD | 400641 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | EAST DORSET | Christchurch Co Const | SZ0842099370 | GB108043011050 | Moors | (S) TRIB OF MOORS RIVER |  |  |  |  | Commissioned in 2018 - full year data expected | 1 | 0 | 0 | 3 | 0.9 | 91.8284 | 1 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011050 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15101B | PATNEY PATNEY WEIR | 401225 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | KENNET | Devizes Co Const | SU0732058240 | GB108043022430 | Etchilhampton Water | RIVER AVON (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 3 | 4 | 0 | 3 | 5.75 | 99.9663 | 2.5 | 5 (installed 2018) | [5 empty] | 2023-10-27 | No sewage litter or sewage fungus | 2023-10-27 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022430 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15115B | CHIRTON SMALL STREET | 401765 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | KENNET | Devizes Co Const | SU0756057260 | GB108043022370 | Hampshire Avon (West) | UNNAMED WATERCOURSE(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 4 | 3 | 0 | 8 | 52 | 100 | 3.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022370 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15117B | DEVIZES DUNKIRK HILL | 101767 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | KENNET | Devizes Co Const | ST9920061910 | GB109053022220 | Summerham Brook | SUMMERHAM BROOK (S) |  |  |  |  | Commissioned in 2020 - full year data expected | 7 | 2 | 11 | 4 | 1.6 | 83.1994 | 6 | 3 (installed 2020) | Telemetry or data archiving failure / issue | Resolved - Dec | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022220 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15123B | SEEND BELL INN / BELL HILL | 102808 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | KENNET | Devizes Co Const | ST9402060810 | GB109053022200 | Semington Bk-Milebourne Str to conf R Avon (Brist) | SUMMERHAM BROOK(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022200 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15129B | POTTERNE WICK | 101814 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | KENNET | Devizes Co Const | SU0006057740 | GB109053022210 | Worton Str - source to conf Semington Bk | WORTON STREAM (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022210 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15158B | OLVESTON THE COMMON | 101837 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST5984087310 | GB109054026650 | Chestle Pill | OLVESTON COMMON RHYNE(S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 4 | 55 | 898.7336 | 99.975 | 29.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026650 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15188B | YATE NORTH ROAD | 101589 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6997083880 | GB109053027590 | Laddon Bk - source to conf R Frome (Brist) | TRIBUTARY OF RIVER FROME(S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 100 | 0 | 1 (installed 2022) | [9 empty] | 2021-12-16 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027590 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15203B | SHILLINGSTONE HAYWARDS BRIDGE | 402500 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH DORSET | North Dorset Co Const | ST8234711999 | GB108043016051 | Stour (Middle u/s Pimperne Brook) | COOKWELL BROOK |  |  |  |  | Commissioned in 2020 - full year data expected |  | 1 | 1 | 0 | 0 | 99.7726 | 0.66667 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016051 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15205B | BLANDFORD ST MARY BOURNEMOUTH ROAD | 402254 | Storm discharge at pumping station |  | Diluted and partially treated | Groundwater | NORTH DORSET | North Dorset Co Const | ST8841405964 | GB108043016051 | Stour (Middle u/s Pimperne Brook) | THE RIVER STOUR |  |  |  |  | Commissioned in 2018 - full year data expected | 3 | 1 | 1 | 2 | 1 | 99.9619 | 1.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016051 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15206B | BLANDFORD LANGTON ROAD (BLANDFORD NO 1) | 401302 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH DORSET | North Dorset Co Const | ST8879006190 | GB108043016052 | Stour (Middle d/s Pimperne Brook) | RIVER STOUR(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 9 | 1 | 3 | 14 | 102.75 | 99.8487 | 6.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016052 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15209B | SPETISBURY CRAWFORD BRIDGE | 402313 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH DORSET | North Dorset Co Const | ST9190501963 | GB108043016052 | Stour (Middle d/s Pimperne Brook) | RIVER STOUR |  |  |  |  | Commissioned in 2017 - full year data expected | 1 | 0 | 0 | 0 | 0 | 99.9374 | 0.33333 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016052 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15230B | POOLE KENNART ROAD | EPRQB3993NE | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | POOLE | Poole Boro Const | SZ0036893124 | 68 | Not part of a river WB catchment | HOLES BAY VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2018 - full year data expected | 7 | 6 | 6 | 11 | 64.1 | 99.5266 | 4.375 | 5 (installed 2018) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15231B | POOLE SANDBANKS PAVILION | 051303 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | POOLE | Poole Boro Const | SZ0436287753 | GB520804415800 | POOLE HARBOUR | POOLE HARBOUR | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA |  |  |  | Commissioned in 2016 - full year data expected | 1 | 7 | 3 | 2 | 1.55 | 99.9165 | 3 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB520804415800 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15236B | POOLE CANFORD HEATH ROAD | 401619 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | POOLE | Mid Dorset and North Poole Co Const | SZ0193394417 | 68 | Not part of a river WB catchment | HATCH POND STREAM |  |  |  |  | Commissioned in 2020 - full year data expected |  | 1 | 0 | 0 | 0 | 86.2437 | 0.33333 | 3 (installed 2020) | Telemetry or data archiving failure / issue | Resolved - Aug |  |  |  | 2021-03-09 | Sewage litter present, no sewage fungus | [5 empty] | No upstream watercourse | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15237B | POOLE MAGNA ROAD | 400714 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | POOLE | Mid Dorset and North Poole Co Const | SZ0452097160 | GB108043011040 | Stour (Lower) | KNIGHTON STREAM(TRIB.R.STOUR) |  |  |  |  | Commissioned in 2018 - full year data expected | 1 | 0 | 0 | 1 | 2.3333 | 99.9739 | 0.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011040 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15240B | POOLE BRANKSOME CHINE | NPSWQD003865 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | POOLE | Poole Boro Const | SZ0678089390 | GB620705550000 | Dorset / Hampshire | ENGLISH CHANNEL |  |  |  |  | Commissioned in 2019 - full year data expected | 15 | 5 | 7 | 13 | 54 | 97.4715 | 8.8 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620705550000 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15246B | CANFORD MAGNA CANFORD MAIN | 040821 | Storm discharge at pumping station |  | Diluted | Rainwater | POOLE | Mid Dorset and North Poole Co Const | SZ0220099000 | GB108043011040 | Stour (Lower) | TRIB RIVER STOUR (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 7 | 5 | 0 | 7 | 20 | 100 | 4.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011040 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15257B | POOLE POOLE BRIDGE POOLE QUAY | 400719 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | POOLE | Poole Boro Const | SZ0063090370 | GB520804415800 | POOLE HARBOUR | BACKWATER CHANNEL,POOLE HARB. | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA |  |  |  | Commissioned in 2018 - full year data expected | 1 | 1 | 1 | 4 | 13.9 | 99.9981 | 1.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB520804415800 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15270B | POOLE CREEKMOOR LANE | 401047 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | POOLE | Poole Boro Const | SZ0037393096 | GB520804415800 | POOLE HARBOUR | HOLES BAY VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2017 - full year data expected | 0 | 1 | 0 | 0 | 0 | 100 | 0.28571 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB520804415800 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15273B | POOLE TURLIN MAIN BLANDFORD ROAD TURLIN MOOR | 400850 | SO on sewer network |  | Diluted and partially treated | Rainwater | POOLE | Poole Boro Const | SY9836092200 | 68 | Not part of a river WB catchment | ROCK LEA RIVER, LYTCHETT BAY | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA | POOLE HARBOUR ROCKLEY SANDS | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=rockl&site=ukk2102-19450 |  | Commissioned in 2019 - full year data expected | 0 | 1 | 7 | 14 | 21.3058 | 99.8677 | 4 | 4 (installed 2019) | [9 empty] | 2022-08-05 | Baseline data, SO not discharging when sampled |  |  | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15275B | POOLE HEWITT ROAD | 402038 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | POOLE | Poole Boro Const | SY9920791809 | GB520804415800 | POOLE HARBOUR | HOLES BAY (VIA SWS) ESTUARINE | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA |  |  |  | Commissioned in 2016 - full year data expected | 2 | 1 | 0 | 0 | 0 | 99.999 | 1.625 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB520804415800 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15282B | BRADFORD ABBAS MILL LANE | 101782 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | ST5869914123 | GB108052015681 | Yeo Us Over Compton | RIVER YEO |  |  |  |  | Commissioned in 2017 - full year data expected | 3 | 4 | 1 | 4 | 27.6914 | 99.9966 | 2 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015681 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15283B | WINCANTON BAYFORD | 402455 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST7248428854 | GB108043015850 | Cale | TRIBUTARY OF THE RIVER CALE |  |  |  |  | Commissioned in 2020 - full year data expected |  | 5 | 1 | 8 | 18.5667 | 99.9939 | 4.6667 | 3 (installed 2020) | [9 empty] | 2022-12-05 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015850 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15284B | HUISH EPISCOPI WAGG DROVE | 071164 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST4354226832 | GB108052021150 | King's Sedgemoor Drain - Henley Sluice to mouth | WAGG DROVE RHYNE |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021150 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15297B | DRAYTON DUCKS LANE | 102400 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST4067024520 | GB108052015470 | Parrett - R Yeo to West Sedgemoor Drain | DRAYTON DRAIN (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 1 | 0 | 5 | 45.5 | 99.9522 | 1.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015470 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15315B | HUISH EPISCOPI WAGG BRIDGE | 071163 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST4405527510 | GB108052021150 | King's Sedgemoor Drain - Henley Sluice to mouth | WAGG RHYNE |  |  |  |  | Commissioned in 2019 - full year data expected | 2 | 4 | 14 | 45 | 775.1833 | 99.6667 | 16.25 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021150 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15320B | LONG SUTTON KNOLE | 103179 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST4846725072 | GB108052015660 | King's Moor Main Drain (Yeo (Somset) | TRIB. OF KINGS MOOR MAIN DRAIN |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 5 | 23 | 245.4667 | 99.9211 | 14 | 1 (installed 2022) | [9 empty] | 2022-06-22 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015660 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15333B | PENSELWOOD PENN MILL | 402000 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST7715431367 | GB108043022490 | Stour (Headwaters) | RIVER STOUR |  |  |  |  | Commissioned in 2019 - full year data expected | 1 | 0 | 1 | 1 | 0.43333 | 100 | 0.6 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022490 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15339B | TEMPLECOMBE SLADES HILL | 401653 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST7065023000 | GB108043015820 | Bow Brook North | BOW BROOK(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 4 | 0 | 0 | 2 | 3.75 | 99.9372 | 1.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015820 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15370C | WESTONZOYLAND LAKEWALL ROAD | 101688 | SO on sewer network |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3506034490 | GB108052021150 | King's Sedgemoor Drain - Henley Sluice to mouth | PIGDITCH RHYNE |  |  |  |  | Commissioned in 2017 - full year data expected | 0 | 1 | 0 | 1 | 3 | 99.9924 | 3.1429 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021150 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15371B | CROSS CROSS EAST | 101667 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Wells Co Const | ST4180454712 | GB109052021540 | Cheddar Yeo - source to conf Stubbingham Rhyne | CROSS RHYNE |  |  |  |  | Commissioned in 2020 - full year data expected |  | 18 | 0 | 19 | 90.5667 | 99.7723 | 12.3333 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021540 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15378B | PAWLETT VICARAGE LANE | 101710 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3016042510 | 200 | Not part of a river WB catchment | TRIB OF PARRETT ESTUARY(S) |  |  |  |  | Commissioned in 2020 - full year data expected | 1 | 0 | 2 | 1 | 5.3333 | 99.9339 | 1 | 3 (installed 2020) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15381B | WEMBDON COMMON | 102688 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST2875237845 | 200 | Not part of a river WB catchment | CROWPILL RHYNE(S) |  |  |  |  | Commissioned in 2020 - full year data expected | 7 | 11 | 7 | 6 | 25.25 | 100 | 7.75 | 3 (installed 2020) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15383B | POOLE EAST QUAY PERRY GARDENS | NPSWQD007062 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | POOLE | Poole Boro Const | SZ0139890251 | GB520804415800 | POOLE HARBOUR | POOLE HARBOUR (ESTAURINE) | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA |  |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 0 | 0 | 0 | 100 | 0.125 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB520804415800 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15389B | PAWLETT MAIN ROAD | 102689 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3019643075 | GB108052021210 | Huntspill | TRIB OF BRICK YARD RHYNE V SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 11 | 11 | 6 | 9 | 71 | 99.898 | 9.25 | 4 (installed 2019) | [9 empty] | 2022-05-20 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021210 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15391B | WESTONZOYLAND HAMROD LANE | 101712 | Storm discharge at pumping station |  | Diluted | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3470034890 | GB108052021150 | King's Sedgemoor Drain - Henley Sluice to mouth | TRIBUTARY OF HAMROD RHYNE |  |  |  |  | Commissioned in 2018 - full year data expected |  |  | 0 | 1 | 1.1 | 99.9391 | 0.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021150 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15394B | SUTTON MALLET | 101687 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3710037022 | GB108052021150 | King's Sedgemoor Drain - Henley Sluice to mouth | TRIB KINGS SEDGEMOOR DRAIN |  |  |  |  | Commissioned in 2017 - full year data expected | 16 | 1 | 0 | 4 | 22.5 | 99.98 | 5.25 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021150 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15396B | WOOLAVINGTON MEADOW FARM | 101713 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3477041910 | GB108052021210 | Huntspill | TRIB OF HUNTSPILL RIVER(S) |  |  |  |  | Commissioned in 2020 - full year data expected | 3 | 7 | 4 | 7 | 43.75 | 98.4561 | 5.25 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021210 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15400B | BRIDGWATER WEST QUAY DRAWBRIDGE | 102693 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3001037410 | 200 | Not part of a river WB catchment | RIVER PARRETT (E) |  | BURNHAM JETTY NORTH | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=burnh&site=ukk2302-35300 |  | Commissioned in 2016 - full year data expected | 1 | 3 | 1 | 2 | 11.4278 | 100 | 1.125 | 7 (installed 2016) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15402B | MIDDLEZOY NETHERMOOR ROAD | 101686 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3777032600 | GB108052021150 | King's Sedgemoor Drain - Henley Sluice to mouth | TRIBUTARY OF SOWY RIVER (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 12 | 8 | 2 | 4 | 23.75 | 99.9741 | 6.5 | 5 (installed 2018) | [9 empty] | 2022-05-20 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021150 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15415B | BRIDGWATER COLLEY LANE | 071342 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3034036390 | 200 | Not part of a river WB catchment | RIVER PARRETT(E) |  | BURNHAM JETTY NORTH | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=burnh&site=ukk2302-35300 |  | Commissioned in 2016 - full year data expected | 0 | 0 | 0 | 14 | 21.2292 | 100 | 6 | 7 (installed 2016) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15436B | RUISHTON BARTON LANE | NPSWQD001438 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST2653725150 | GB108052015482 | Tone Ds Taunton | THE RIVER TONE |  |  |  |  | Commissioned in 2020 - full year data expected |  | 6 | 0 | 4 | 42.2322 | 100 | 3.3333 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015482 | Yes |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15443C | TAUNTON NEW BARN QUEENSWAY | 103194 | SO on sewer network |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST2074523409 | GB108052015410 | Sherford Stream | GALMINGTON STREAM VIA SWS |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 0 | 0 | 0 | 99.9103 | 0 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015410 | Yes |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15447C | TAUNTON MOUNTWAY BISHOPS HULL | 103408 | SO on sewer network |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST2094724968 | GB108052015482 | Tone Ds Taunton | RIVER TONE |  |  |  |  | Commissioned in 2017 - full year data expected | 7 | 2 | 2 | 9 | 24.6761 | 100 | 5.4286 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015482 | Yes |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15448B | TAUNTON LONGACRE CLOSE | 103187 | Storm discharge at pumping station |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST2249626314 | GB108052015482 | Tone Ds Taunton | KINGSTON STREAM(S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 100 | 0 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015482 | Yes |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15454B | CREECH ST MICHAEL NORTH END | 102019 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST2729426222 | GB108052015482 | Tone Ds Taunton | TRIB OF RIVER TONE |  |  |  |  | Commissioned in 2020 - full year data expected |  | 2 | 0 | 4 | 21.4192 | 99.9935 | 2 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015482 | Yes |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15457B | WELLINGTON WESTFORD | 100532/PC/01 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST1236020520 | GB108052015380 | Westford Stream | WESTFORD STREAM |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 4 | 13 | 60.2667 | 99.4962 | 8.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015380 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15458B | STOKE ST GREGORY CURLOAD | 102570 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST3393627986 | 200 | Not part of a river WB catchment | RIVER TONE |  |  |  |  | Commissioned in 2017 - full year data expected | 0 | 0 | 0 | 11 | 13.5362 | 99.9277 | 3.3333 | 6 (installed 2017) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15460B | MEARE GREEN STOKE ST GREGORY | 070896 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST3340326343 | GB108052015450 | West Sedgemoor Main Drain | TRIB OF SEDGEMOOR OLD RHYNE |  |  |  |  | Commissioned in 2019 - full year data expected | 2 | 0 | 1 | 1 | 8.5 | 100 | 1 | 4 (installed 2019) | [9 empty] | 2022-01-17 | No impact (POI 0.59mg/l, DS 0.59mg/l) |  | Upstream inaccessible | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015450 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15467B | NAILSBOURNE | 103191 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST2143928401 | GB108052015490 | Tributary of Back Stream (Tone Catchment) | TRIB OF THE BACK STREAM |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 6 | 21 | 108.6527 | 100 | 13.5 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015490 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15500B | BRADPOLE FISHWEIR FOUL | 402030 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | SY4789193755 | GB108044009580 | Asker | RIVER ASKER VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 2 | 0 | 0 | 3 | 8.6333 | 97.2175 | 1 | 5 (installed 2018) | [9 empty] | 2021-11-17 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009580 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15527B | DUNKERTON BROOKLANDS | 021688 | Storm discharge at pumping station |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST7100059400 | GB109053022290 | Cam Bk - source to conf Wellow Bk | TRIB OF MIDFORD BROOK (S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 1 | 7 | 67.7833 | 99.9935 | 4 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022290 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15536B | WELLOW MILL HILL | 103601 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST7417058080 | GB109053022271 | Wellow Bk - Snails Bk to Bristol Avon | WELLOW BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 1 | 3 | 1 | 0 | 0 | 99.8989 | 3.5 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022271 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15548B | KEYNSHAM KEYNSHAM LOW LEVEL | 102124 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6568068530 | GB109053021950 | Chew - conf Winford Bk to conf R Avon (Brist) | RIVER CHEW |  |  |  |  | Commissioned in 2017 - full year data expected | 8 | 9 | 7 | 27 | 203.8 | 100 | 13.5 | 6 (installed 2017) | [9 empty] | 2022-01-11 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021950 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15553C | PORTLAND VICTORIA SQUARE | 040206 | Storm discharge at pumping station |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6851074510 | GB680805270000 | Portland Harbour | PORTLAND HARBOUR | PORTLAND NORTH EASTERN BREAKWATER | PORTLAND HARBOUR CASTLE COVE/PORTLAND HARBOUR SANDSFOOT CASTLE | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=castle%20co&site=ukk2206-20800 | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=sandsf&site=ukk2206-20900 | Commissioned in 2016 - full year data expected | 2 | 9 | 6 | 12 | 3.0103 | 100 | 5.125 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB680805270000 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15555B | WYKE REGIS HILLCREST ROAD | 402476 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6729077210 | GB680805270000 | Portland Harbour | PORTLAND HARBOUR | PORTLAND NORTH EASTERN BREAKWATER | PORTLAND HARBOUR CASTLE COVE/PORTLAND HARBOUR SANDSFOOT CASTLE | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=castle%20co&site=ukk2206-20800 | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=sandsf&site=ukk2206-20900 | Commissioned in 2016 - full year data expected | 2 | 0 | 0 | 4 | 1.75 | 94.9838 | 1.25 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB680805270000 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15556B | WEYMOUTH RADIPOLE | 401048 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6766079210 | GB510804415700 | WEY | WEYMOUTH HARBOUR (E) |  | WEYMOUTH CENTRAL | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=weymouth&site=ukk2206-20700 |  | Commissioned in 2016 - full year data expected | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB510804415700 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15559B | PORTLAND PENNSYLVANIA ROAD | 402253 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6961071170 | 2 | Not part of a river WB catchment | GROUND |  | CHURCH OPE COVE | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=church%20op&site=ukk2206-20500 |  | Commissioned in 2016 - full year data expected | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 7 (installed 2016) | [9 empty] | 2021-11-18 | Baseline data, SO not discharging when sampled |  |  | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15561B | WEYMOUTH FERRYBRIDGE PORTLAND ROAD | 402477 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6659076230 | GB510080077000 | Fleet Lagoon | THE FLEET | PORTLAND NORTH EASTERN BREAKWATER | PORTLAND HARBOUR CASTLE COVE/PORTLAND HARBOUR SANDSFOOT CASTLE** | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=castle%20co&site=ukk2206-20800 | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=sandsf&site=ukk2206-20900 | Commissioned in 2016 - full year data expected | 0 | 0 | 0 | 0 | 0 | 99.8621 | 0 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB510080077000 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15572B | LOCKING LOCKING VILLAGE | 100524/PC/01 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH SOMERSET | Weston-Super-Mare Co Const | ST3574060250 | GB109052021590 | Uphill Great Rhyne - source to conf R Axe Estuary | TRIB OF UPHILL GREAT RHNE |  |  |  |  | Commissioned in 2019 - full year data expected | 0 | 4 | 5 | 9 | 39.4167 | 99.941 | 5.4 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021590 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15574B | SANDFORD BATCH | 103602 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH SOMERSET | Weston-Super-Mare Co Const | ST4181558833 | GB109052021620 | Oldbridge R - source to nr Manor Fm | TOWERHEAD BROOK |  |  |  |  | Commissioned in 2020 - full year data expected |  | 2 | 2 | 6 | 16.4667 | 99.882 | 3.3333 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021620 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15577B | SANDFORD SANDMEAD LANE | 103173 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH SOMERSET | Weston-Super-Mare Co Const | ST4246160065 | GB109052021620 | Oldbridge R - source to nr Manor Fm | SANDMEAD RHYNE |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 2 | 32 | 336.2333 | 99.9502 | 17 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021620 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15622B | CLEVEDON MARINE PARADE | 071176 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH SOMERSET | North Somerset Co Const | ST4026072080 | GB530905415405 | BRISTOL AVON | SEVERN ESTUARY(E) |  | CLEVEDON BEACH | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=cleved&site=ukk1202-36000 |  | Commissioned in 2016 - full year data expected | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15644B | SUTTON WALDRON | 041782 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH DORSET | North Dorset Co Const | ST8643015260 | GB108043016080 | Fontmell Brook | TRIBUTARY OF FONTMELL BROOK |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 0 | 0 | 0 | 100 | 0 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016080 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15715B | BRIDGWATER HORSEY BATH ROAD | 101841 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3234039080 | GB108052021150 | King's Sedgemoor Drain - Henley Sluice to mouth | BATH ROAD RHYNE(S) |  |  |  |  | Commissioned in 2019 - full year data expected | 1 | 5 | 2 | 1 | 3.9167 | 99.8191 | 2.2 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021150 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15718C | BISHOPS HULL SHUTEMEAD | EPRJB3795EQ | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST2018424765 | GB108052015481 | Tone - Wellington to Taunton | TRIB OF RIVER TONE VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected |  | 11 | 7 | 6 | 61.4833 | 99.5622 | 8 | 3 (installed 2020) | [5 empty] | 2020-04-23 | No sewage litter or sewage fungus | 2020-10-22 | Lab assessment - No impact |  |  |  | RICT analysis complete (Extremely severe) | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015481 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15723B | TETBURY SPRINGFIELDS | 103899 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | COTSWOLD | The Cotswolds Co Const | ST8969093420 | GB109053027800 | Tetbury Avon - source to conf unnamed trib | THE RIVER AVON(TETBURY BRANCH) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 100 | 0 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027800 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15792C | WESTON-SUPER-MARE KNIGHTSTONE ROAD | 072435 | Storm discharge at pumping station |  | Diluted | Rainwater | NORTH SOMERSET | Weston-Super-Mare Co Const | ST3145061880 | GB540805210900 | PARRETT | WESTON BAY (E) |  | WESTON-SUPER-MARE UPHILL SLIPWAY/WESTON MAIN | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=weston&site=ukk1202-35700 | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=weston&site=ukk1202-35800 | Commissioned in 2016 - full year data expected | 0 | 1 | 0 | 0 | 0 | 100 | 0.75 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB540805210900 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16000C | WELLINGTON CORAMS LANE | 072548 | SO on sewer network |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST1292520886 | GB108052015380 | Westford Stream | BACK STREAM VIA SWS |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 0 | 0 | 0 | 100 | 0 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015380 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16035C | BATH HUNGERFORD ROAD / UPPER BRISTOL ROAD JUNCTION | 010911 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7347065006 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 4 | 3 | 2 | 0.13333 | 97.4045 | 2.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16048C | BATH ST JOHNS ROAD OPP VULCAN HOUSE | 102822 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7520765401 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 15 | 10 | 6 | 3 | 0.36667 | 99.9916 | 4.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16049C | BATH WARMINSTER ROAD / SYDNEY ROAD JUNCTION | 102823 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7589265479 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | KENNET & AVON CANAL(VIA SWS) |  |  |  |  | Commissioned in 2018 - full year data expected | 2 | 3 | 1 | 1 | 0.23333 | 99.7717 | 5.625 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16052C | BATH BRASSMILL LANE BETWEEN OSBOURN / AVONDALE ROAD | 010922 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7240764929 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 7 | 5 | 3 | 15 | 73.1667 | 99.9971 | 6.2 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16053C | BATH LOWER BRISTOL ROAD NEAR MILL LANE | 010920 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7275264761 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 6 | 4 | 3 | 0.16667 | 99.9403 | 3 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16061C | BATH GROVE STREET OPP NO 13 | 101184 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7516165112 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 100 | 0.125 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16063C | BATH RIVERSIDE WALK OLD CATTLE MARKET WALCOT | 010873 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7514265194 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 8 | 8 | 35.9333 | 99.9467 | 8 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16064C | BATH GROVE STREET / ST JOHNS STREET JUNC NR BETHEL CH | 101185 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7517065213 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 8 | 9 | 2 | 1 | 0.26667 | 99.5723 | 4.125 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16069C | BATH LOOP ROAD WALCOT STREET CAR PARK | 101187 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7515764977 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 4 | 1 | 2 | 0 | 0 | 99.723 | 2.1429 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16084C | BATH HAMPTON ROW / ROCKLIFFE AVENUE R/O (NR BATHS) | 010850 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7586765808 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 3 | 2 | 1 | 3 | 14.7 | 99.7523 | 1.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16089C | BATH NEWMARKET ROW GRAND PARADE | NPSWQD010266 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7520564894 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 1 | 1 | 0 | 0 | 99.6686 | 0.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16122C | BATH SOUTHDOWN ROAD O/S NO 85 NR GLEBE ROAD JUNCTION | 101928 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7341064930 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 1 | 0 | 0 | 1 | 1.6333 | 87.4791 | 0.4 | 5 (installed 2018) | Telemetry or data archiving failure / issue | Resolved - Mar | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16125C | BATH LYMORE GARDENS O/S NO 15 ADJ LAUNDRY | 101931 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7343064930 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 99.414 | 0.4 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16147C | BRISTOL WATLING WAY IN GARDEN NO 27 | 102071 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5202277004 | GB530905415405 | BRISTOL AVON | RIVER AVON (ESTUARINE) VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 7 | 5 | 4 | 0.53333 | 99.9996 | 4 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16159C | BRISTOL BRISTOL ROAD / SALTWELL VIADUCT | 100579/CS/01 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6131468247 | GB109053021980 | Brislington Bk - source to conf R Avon (Brist) | TRIB OF BRISLINGTON BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 100 | 0 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021980 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16160C | BRISTOL BROOMHILL ROAD / HUBERT CLOSE | 100587/CS/01 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6339670669 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 1 | 0 | 0 | 99.7481 | 3.2 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16167C | BRISTOL MAXSE ROAD JUNCTION MARSTON ROAD | 013224 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST6091969974 | GB109053021980 | Brislington Bk - source to conf R Avon (Brist) | BRISLINGTON BROOK VIA SWS |  |  |  |  | Commissioned in 2021 - full year data expected |  | 0 | 0 | 0 | 0 | 99.9182 | 0 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021980 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16170C | BRISTOL SCHOOL ROAD O/S NO 112 | 100583/CS/01 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6218470988 | GB109053021980 | Brislington Bk - source to conf R Avon (Brist) | BRISLINGTON BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 1 | 2 | 4 | 2 | 0.63333 | 95.2607 | 2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021980 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16171C | BRISTOL SIDCOT | 100585/CS/01 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6339670669 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 3 | 3 | 4 | 1 | 0.066667 | 98.868 | 3.6 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16172C | BRISTOL SIDCOT O/S NO 8 | 100586/CS/01 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6339070670 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON(S) |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 1 | 1 | 0.2 | 99.8912 | 1 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16173C | BRISTOL SOMERDALE AVENUE / SALCOMBE ROAD | 100576/CS/01 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST6027469895 | GB109053021980 | Brislington Bk - source to conf R Avon (Brist) | BRISLINGTON BROOK VIA SWS |  |  |  |  | Commissioned in 2021 - full year data expected |  | 0 | 0 | 0 | 0 | 99.7549 | 0 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021980 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16177C | BRISTOL WELLS ROAD/MARSTON ROAD | 013219 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST6091969974 | GB109053021980 | Brislington Bk - source to conf R Avon (Brist) | BRISLINGTON BROOK VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 100 | 0 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021980 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16178C | BRISTOL WELLS ROAD / GREENMORE ROAD | 013223 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST6092269972 | GB109053021980 | Brislington Bk - source to conf R Avon (Brist) | BRISLINGTON BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 1 | 0.033333 | 99.9741 | 0.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021980 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16183C | BRISTOL WHITBY ROAD NEAR BLOOMFIELD ROAD | 100588/CS/01 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6113871930 | 157 | Not part of a river WB catchment | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 1 | 0.96667 | 92.2854 | 0.25 | 5 (installed 2018) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16186C | BRISTOL BOND STREET O/S CAR PARK | 101093 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5948073340 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 4 | 6 | 3 | 2 | 1.7333 | 100 | 3 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16188C | BRISTOL BROADMEAD ON HUB | 101089 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5921973244 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 99.8866 | 0 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16189C | BRISTOL BROADMEAD / PENN STREET | 101091 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5938373282 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 1 | 6 | 10.8 | 92.051 | 3.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16192C | BRISTOL CHRISTMAS STEPS AT THE BOTTOM | 101082 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5867973165 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 1 | 0.2 | 99.9912 | 0.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16196C | BRISTOL HOTWELLS ROAD APPROX NO 100 | 102899 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5757772464 | 157 | Not part of a river WB catchment | BRISTOL FROME FLOATING HARBOUR |  |  |  |  | Commissioned in 2018 - full year data expected | 11 | 8 | 3 | 11 | 6.6333 | 99.7348 | 7.75 | 5 (installed 2018) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16198C | BRISTOL LEWIN MEAD O/S GREYFRIARS | 101083 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5871573252 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 99.7774 | 0 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16201C | BRISTOL NEWFOUNDLAND ROAD / PRITCHARD STREET | 101092 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5953773366 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 99.7504 | 0 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16202C | BRISTOL NURSING SCHOOL MARLBOROUGH STREET | 101087 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5918473222 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 3 | 6 | 2 | 2 | 0.33333 | 99.6621 | 3.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16206C | BRISTOL SILVER ST/BROADMEAD | 101086 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5895473267 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 0 | 0 | 0 | 96.524 | 0 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16208C | BRISTOL WELLINGTON ROAD PLAYGROUND | 101094 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5957673396 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 4 | 6 | 3 | 2 | 1.8333 | 99.9022 | 3 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16213C | BRISTOL BLACKBERRY HILL O/S NO 9 FROME BRIDGE | 101239 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6212276467 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 99.4852 | 0 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16214C | BRISTOL BRENTRY ROAD O/S NO 57 | 101244 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6183775665 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 1 | 1 | 0.033333 | 99.7511 | 0.875 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16216C | BRISTOL BURCHILLS GREEN ROAD O/S NO 164 | 101247 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6364374489 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | COOMBE BROOK VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 3 | 3 | 0.1 | 99.9996 | 3 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16222C | BRISTOL FILWOOD ROAD / GOODNESTON ROAD | 101279 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6238075800 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | FISHPONDS BROOK VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 1 | 2 | 0 | 0 | 90.0476 | 0.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16226C | BRISTOL FOUNDRY LANE OPEN SPACE | 101238 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6233174958 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | COOMBE BROOK VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 100 | 0 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16229C | BRISTOL FRENCHAY PARK ROAD NO 46A | 101240 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6213076480 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME(VIA A SWS) |  |  |  |  | Commissioned in 2018 - full year data expected | 14 | 13 | 8 | 26 | 26.6333 | 95.957 | 9.875 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16230C | BRISTOL FRENCHAY PARK ROAD O/S NO 201 | 101241 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6313577387 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | TRIB OF THE RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 82.132 | 0.125 | 5 (installed 2018) | Sensor failure / issue | Resolved - Nov | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16233C | BRISTOL FACTORY R/O GORDON ROAD | 102144 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST6094074930 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME VIA SWS |  |  |  |  | Commissioned in 2017 - full year data expected | 0 | 1 | 1 | 0 | 0 | 99.9902 | 0.28571 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16234C | BRISTOL GREENBANK VIEW | 101242 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6093874927 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 9 | 16 | 13.1667 | 99.949 | 12.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16235C | BRISTOL GROVE ROAD NEAR FISHPONDS ROAD | 101277 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6238075800 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | FISHPONDS BROOK (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 2 | 1 | 0 | 0 | 95.5285 | 0.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16236C | BRISTOL GROVE ROAD O/S NO 31 | 101281 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6238075804 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | FISHPONDS BROOK VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected |  | 1 | 1 | 0 | 0 | 99.8311 | 0.66667 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16237C | BRISTOL GROVE ROAD O/S NO 41 | 101278 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6238075800 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | FISHPONDS BROOK (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 1 | 0 | 0 | 0 | 0 | 100 | 0.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16244C | BRISTOL LODGE CAUSEWAY O/S 147 | 101234 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6323174958 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | COOMBE BROOK VIA SWS |  |  |  |  | Commissioned in 2021 - full year data expected |  | 1 | 2 | 2 | 0.46667 | 98.4159 | 1.6667 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16251C | BRISTOL PARNALLS FACTORY | 101282 | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol East Boro Const | ST6238075800 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | FISHPONDS BROOK (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 16 | 10 | 3 | 15 | 18.7 | 99.8459 | 11 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16256C | BRISTOL SPEEDWELL ROAD O/S NO 415 | 101248 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6354474489 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | TRIBUTARY OF COOMBE BROOK |  |  |  |  | Commissioned in 2020 - full year data expected |  | 11 | 4 | 3 | 0.3 | 95.0738 | 6 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16261C | BRISTOL BEDMINSTER ROAD CYCLE TRACK | 101670 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST5848570885 | GB109053021970 | The Malago - source to conf R Avon (Brist New Cut) | THE MALAGO |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 0 | 0 | 0 | 98.8626 | 0 | 2 (installed 2021) | [5 empty] | 2023-09-19 | No sewage litter or sewage fungus | 2023-09-19 | TBC |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021970 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16269C | BRISTOL EAST STREET | 102898 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST5832671454 | GB109053021970 | The Malago - source to conf R Avon (Brist New Cut) | SHEENE ROAD CULVERT |  |  |  |  | Commissioned in 2018 - full year data expected | 11 | 0 | 0 | 2 | 0.1 | 97.3718 | 3.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021970 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16270C | BRISTOL FORTFIELD ROAD O/S NO 166 | 102979 | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol South Boro Const | ST5819669123 | GB109053021970 | The Malago - source to conf R Avon (Brist New Cut) | PIGEONHOUSE STREAM VIA SWS |  |  |  |  | Commissioned in 2017 - full year data expected | 3 | 0 | 0 | 0 | 0 | 99.9782 | 3.5714 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021970 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16281C | BRISTOL PARSON STREET / NOVERS HILL | 101823 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST5834070333 | GB109053021970 | The Malago - source to conf R Avon (Brist New Cut) | THE MALAGO VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected |  | 0 | 0 | 0 | 0 | 99.9056 | 0 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021970 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16286C | BRISTOL TUGELA ROAD O/S NO 18 | 101825 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST5724069020 | GB109053021970 | The Malago - source to conf R Avon (Brist New Cut) | THE MALAGO (VIA SWS) |  |  |  |  | Commissioned in 2018 - full year data expected | 1 | 1 | 1 | 2 | 0.53333 | 99.6142 | 2.375 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021970 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16287C | BRISTOL VALE LANE | 101826 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol South Boro Const | ST5803969822 | GB109053021970 | The Malago - source to conf R Avon (Brist New Cut) | THE MALAGO |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 99.9996 | 0 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021970 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16301C | SHEPTON MALLET VICTORIA GROVE/CHARLTON ROAD | 100505/CS/01 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Wells Co Const | ST6276843525 | GB108052021221 | Sheppey | RIVER SHEPPEY VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected |  | 2 | 0 | 0 | 0 | 99.9954 | 0.66667 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021221 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16304C | BRISTOL GLOUCESTER ROAD O/S NO 199 | 013054 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5612074459 | 157 | Not part of a river WB catchment | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 5 (installed 2018) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16308C | STREET FARM LANE | 102379 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Wells Co Const | ST4816837162 | GB108052021181 | South Drain | SOUTH DRAIN |  |  |  |  | Commissioned in 2017 - full year data expected | 7 | 12 | 14 | 17 | 31.4167 | 99.9965 | 9.7143 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021181 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16312C | BRISTOL SOMMERVILLE ROAD / NORTH ROAD | 100875 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5611874456 | GB530905415405 | BRISTOL AVON | RIVER AVON (ESTUARINE) VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 1 | 0.066667 | 78.9543 | 0.25 | 5 (installed 2018) | Comms failure / issue | Resolved - Dec | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16315C | BRISTOL BROOK ROAD CAR PARK J SOMERS & SONS | 101790 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST5611874456 | GB530905415405 | BRISTOL AVON | RIVER AVON (E) VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 1 | 0 | 0 | 0 | 0 | 99.653 | 0.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16327C | BRISTOL LYPPIATT ROAD O/S NO 29 | 102879 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5611874456 | GB530905415405 | BRISTOL AVON | RIVER AVON (E) VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 99.8573 | 0 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16328C | BRISTOL LYPPIATT ROAD O/S NO 57 | 102880 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5612074460 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2021 - full year data expected |  | 1 | 0 | 1 | 0.066667 | 100 | 0.66667 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16329C | BRISTOL MARION WALK O/S NO 4 | 103312 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6274872843 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 2 | 0 | 0 | 0 | 0 | 99.8314 | 0.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16339C | BRISTOL SPEEDWELL ROAD O/S NO 34 | 102882 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST5611874456 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2018 - full year data expected | 3 | 1 | 1 | 0 | 0 | 99.9091 | 1.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16353C | BRISTOL LANDSEER AVENUE O/S NO 50 | 011093 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST6056277033 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | TRIB OF HORFIELD BROOK VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 5 | 6 | 4 | 13 | 41.7333 | 96.4098 | 7 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16359C | BRISTOL ROWLANDSON GARDENS NO 24 | 101729 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST6056277033 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | TRIB OF HORFIELD BROOK VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected | 4 | 13 | 7 | 22 | 81.8 | 99.8562 | 11.5 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16362C | BRISTOL SUSSEX PLACE R/O NO 48 | 101880 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST6000974495 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | GROUNDWATER VIA INFILT SYSTEM |  |  |  |  | Commissioned in 2021 - full year data expected |  | 0 | 0 | 0 | 0 | 100 | 0 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16376C | BRISTOL HENBURY ROAD O/S NO 47 | 100844 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5697377614 | GB109053027530 | Trym - source to conf R Avon (Brist) | RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 1 | 0 | 0 | 100 | 0.25 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16387C | BRISTOL OAKWOOD ROAD O/S NO 21 | 100475 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5801977358 | GB109053027530 | Trym - source to conf R Avon (Brist) | TRIB OF RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 2 | 4 | 1 | 1 | 0.033333 | 99.9996 | 2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16388C | BRISTOL ROCKSIDE DRIVE O/S NO 2 | 100474 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5801877357 | GB109053027530 | Trym - source to conf R Avon (Brist) | TRIBUTARY OF RIVER TRYM VIA SW |  |  |  |  | Commissioned in 2021 - full year data expected |  | 0 | 1 | 0 | 0 | 99.8965 | 0.33333 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16392C | BRISTOL SEA MILLS LANE NR BRIDGE | 100840 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5488075830 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2019 - full year data expected | 3 | 0 | 0 | 2 | 2.5833 | 99.9971 | 0.83333 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16403C | BRISTOL WELLINGTON HILL WEST NO 147 (NO 1) | 100463 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5815577315 | GB109053027530 | Trym - source to conf R Avon (Brist) | TRIB OF RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 99.7546 | 0 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16404C | BRISTOL WELLINGTON HILL WEST NO 147 (NO 2) | 100465 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5815577315 | GB109053027530 | Trym - source to conf R Avon (Brist) | TRIB OF RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 74.0011 | 0 | 5 (installed 2018) | Comms failure / issue | Resolved - Apr | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16416C | BRISTOL CLARE STREET | 101081 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5856872056 | 157 | Not part of a river WB catchment | RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 99.586 | 0 | 1 (installed 2022) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16418C | BRISTOL ST JAMES BARTON | 101088 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5918473221 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 1 | 0 | 3 | 0.3 | 67.2462 | 1 | 5 (installed 2018) | Sensor failure / issue | Scheduled | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16423C | BRISTOL PORTWAY BRIDGE | 100841 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5488075830 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2017 - full year data expected | 2 | 1 | 0 | 3 | 4.3333 | 99.6785 | 3.2857 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16438C | BRISTOL BROADMEAD / SILVER STREET | 101085 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5895273261 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 99.7546 | 0 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16440C | BRISTOL MAGGS LANE OPEN SPACE | 101237 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6233074958 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | COOMBE BROOK VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 99.8516 | 0 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16448C | EASTERTON MANOR HOUSE | 101816 | SO on sewer network |  | Diluted | Rainwater | KENNET | Devizes Co Const | SU0209554817 | GB109053022130 | Semington Bk - source to conf Worton Str | EASTERTON BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 5 | 5 | 2 | 4 | 2.6333 | 99.602 | 4 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022130 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16449C | POULSHOT MILL LANE | 102477 | SO on sewer network |  | Diluted | Rainwater | KENNET | Devizes Co Const | ST9661858872 | GB109053022190 | Poulshot Str - source to conf Summerham Bk | TRIB OF SUMMERHAM BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 97.1142 | 0 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022190 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16455C | DEVIZES VALLEY SEWER | 101768 | SO on sewer network |  | Diluted | Rainwater | KENNET | Devizes Co Const | ST9994061300 | GB109053022190 | Poulshot Str - source to conf Summerham Bk | POULSHOT STREAM |  |  |  |  | Commissioned in 2018 - full year data expected | 2 | 3 | 2 | 1 | 0.43333 | 94.7934 | 1.8333 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022190 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16467C | BRISTOL HANHAM FOOTSHILL ROAD | 101757 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6289872188 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON (VIA SWS) |  |  |  |  | Commissioned in 2018 - full year data expected | 2 | 8 | 4 | 9 | 0.83333 | 99.7865 | 3 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16468C | BRISTOL HANHAM HIGH STREET | 101758 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6289672188 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON (VIA SWS) |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 99.7546 | 0 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16473C | BRISTOL KINGSWOOD WOODSIDE ROAD | 101752 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6403473339 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | CONHAM VALE STREAM VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 1 | 0 | 0 | 0 | 0 | 99.833 | 0.25 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16482C | BRISTOL KINGSWOOD NEW CHELTENHAM ROAD NO 84 | 100896 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6631974374 | GB109053027450 | Siston Bk - source to conf R Avon (Brist) | WARMLEY BROOK VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 3 | 35 | 82.4 | 81.6396 | 19 | 1 (installed 2022) | Telemetry or data archiving failure / issue | Resolved - Dec | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027450 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16486C | BRISTOL KINGSWOOD HOLLY HILL ROAD / NEW CHELTENHAM ROAD JUNCTION | 100898 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6631974374 | GB109053027450 | Siston Bk - source to conf R Avon (Brist) | WARMLEY BROOK VIA SWS |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 5 | 9 | 3.2333 | 100 | 7 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027450 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16488C | BRISTOL KINGSWOOD HILL STREET | 101749 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6672572837 | GB109053027450 | Siston Bk - source to conf R Avon (Brist) | SISTON BROOK VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 2 | 4 | 0 | 6 | 0.53333 | 65.6385 | 3 | 4 (installed 2019) | Capital / maintenance works affect EDM operation | Resolved - May | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027450 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16489C | BRISTOL KINGSWOOD ORCHARD ROAD | 101760 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6672572837 | GB109053027450 | Siston Bk - source to conf R Avon (Brist) | SISTON BROOK VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 16 | 7 | 2 | 7 | 0.53333 | 96.9524 | 8 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027450 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16491C | BRISTOL WARMLEY MILL LANE AT REAR | 101763 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6703372385 | GB109053027450 | Siston Bk - source to conf R Avon (Brist) | SISTON BROOK (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 5 | 2 | 4 | 2 | 0.3 | 99.7546 | 12.2 | 5 (installed 2018) | [5 empty] | 2021-05-09 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027450 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16500C | CROSCOMBE MANOR HOUSE OPP | 102500 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Wells Co Const | ST5892944332 | GB108052021221 | Sheppey | RIVER SHEPPEY (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 4 | 2 | 3 | 0 | 0 | 99.4802 | 2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021221 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16505C | FROME SINGERS CATTLE MARKET | 100442 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Somerton and Frome Co Const | ST7770348110 | GB109053022101 | Frome (Maiden Bradley to Mells) | RIVER FROME VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 13 | 12 | 13 | 16 | 3.1667 | 99.6747 | 10.7143 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022101 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16511C | FROME NORTH OF CARPET FACTORY NEAR RAILWAY JUNCTION | 102703 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Somerton and Frome Co Const | ST7859247954 | GB109053022101 | Frome (Maiden Bradley to Mells) | RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 8 | 8 | 7 | 7 | 1.5667 | 99.7549 | 11 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022101 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16512C | FROME WALLBRIDGE | 100445 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Somerton and Frome Co Const | ST7866047800 | GB109053022101 | Frome (Maiden Bradley to Mells) | RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 6 | 7 | 5 | 4 | 1.5333 | 99.7314 | 5.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022101 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16523C | NUNNEY MARKET PLACE SOUTH END | 102501 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Somerton and Frome Co Const | ST7366845705 | GB109053022000 | Nunney Bk - source to conf Mells R | NUNNEY BROOK(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 1 | 6 | 4 | 6 | 1.7667 | 96.9486 | 4.2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022000 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16525C | SHEPTON MALLET SHAFTGATE AV NO 82/84 | NPSWQD010269 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Wells Co Const | ST6132743766 | GB108052021221 | Sheppey | GROUNDWATER VIA INFILT SYSTEM |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 1 | 0 | 0 | 99.9962 | 0.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021221 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16540C | STREET GLASTON ROAD OPP 30 | 100742 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Wells Co Const | ST4858337198 | GB108052021181 | South Drain | TRIB OF SOUTH DRAIN |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 9 | 5 | 14.8333 | 99.6849 | 7 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021181 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16541C | STREET STRODE ROAD ALLOTMENTS | 102490 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Wells Co Const | ST4932036984 | GB108052021181 | South Drain | OLD RHYNE VIA SWS |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 1 | 2 | 15.1667 | 100 | 1.5 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021181 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16546C | RODE BARROW FARM TANK | 100190 | SO on sewer network |  | Diluted and partially treated | Rainwater | MENDIP | Somerton and Frome Co Const | ST8026554191 | GB109053021840 | Somerset Frome conf with Mells to conf B. Avo | TRIB OF THE RIVER FROME |  |  |  |  | Commissioned in 2018 - full year data expected | 8 | 2 | 3 | 4 | 20.3667 | 99.7549 | 4 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16566C | CALNE OXFORD ROAD / WOOD STREET | 100774 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9987571047 | GB109053022050 | Marden - source to conf Cowage Bk | RIVER MARDEN VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 2 | 2 | 1 | 1 | 0.26667 | 99.7549 | 1.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022050 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16569C | CHIPPENHAM COMMONS SLIP | 100810 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | Chippenham Co Const | ST9244773148 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 99.527 | 0 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16575C | BRINKWORTH FOUL SEW O/F | 102887 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | SU0237985528 | GB109053027760 | Woodbridge Bk - source to conf Charlton Str | WOODBRIDGE BROOK |  |  |  |  | Commissioned in 2020 - full year data expected | 0 | 1 | 1 | 3 | 5.8 | 93.0308 | 1.25 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027760 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16579C | MALMESBURY HARPERS LANE | 012854 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9294287274 | GB109053027690 | Sherston Avon | RIVER AVON (SHERSTON BRANCH) |  |  |  |  | Commissioned in 2018 - full year data expected | 5 | 7 | 7 | 4 | 1.1 | 92.645 | 4.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027690 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16592C | ROYAL WOOTTON BASSETT NEW ROAD | 103862 | SO on sewer network |  | Diluted and partially treated | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | SU0643581903 | GB109053027740 | Brinkworth Brook | WESTBURY PARK W/C VIA SWS |  |  |  |  | Commissioned in 2021 - full year data expected |  | 1 | 0 | 3 | 15.2417 | 99.0992 | 1.3333 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027740 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16603C | CHIPPENHAM THE IVY | 100820 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | Chippenham Co Const | ST9191173041 | GB109053027440 | Avon (Brist) conf R Marden to conf Semington Bk | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 1 | 0.56667 | 94.8337 | 0.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027440 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16641C | SALISBURY CHURCHILL GARDENS NEAR COLLEGE | 043198 | SO on sewer network |  | Diluted | Rainwater | SALISBURY | Salisbury Co Const | SU1486029420 | GB108043015840 | Hampshire Avon (Lower) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 99.8904 | 0 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043015840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16653C | MERE GARAGE ADJ TO | 401450 | SO on sewer network |  | Diluted | Rainwater | SALISBURY | South West Wiltshire Co Const | ST8153132490 | GB108043022450 | Shreen Water (including Ashfield Water) | SHREEN WATER |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 4 | 9 | 3.1667 | 99.5141 | 6.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022450 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16654C | MERE WHITE ROAD | 401451 | SO on sewer network |  | Diluted | Rainwater | SALISBURY | South West Wiltshire Co Const | ST8153932473 | GB108043022450 | Shreen Water (including Ashfield Water) | SHREEN WATER |  |  |  |  | Commissioned in 2020 - full year data expected |  | 6 | 4 | 6 | 3.1667 | 99.9741 | 5.3333 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022450 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16677C | STOKE SUB HAMDON WINDSOR LANE | 100710 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST4849717533 | GB108052015350 | Wellhams Brook | TRIB OF WELLHAMS BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 7 | 6 | 15.3667 | 99.7873 | 6.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015350 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16680C | MARTOCK CHURCH HOUSE WATER STREET | 013157 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST4611319072 | GB108052015350 | Wellhams Brook | MILL BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 1 | 1 | 2 | 14.9333 | 100 | 1 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015350 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16689C | YEOVIL WYNDHAM HILL | 071731 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5639515975 | GB108052015600 | Dodham Brook (Yeo (Somset)) | DODHAM BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 4 | 4 | 2 | 99.5753 | 4 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015600 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16690C | YEOVIL PRESTON GROVE O/S 2 | 102260 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5489815994 | GB108052015600 | Dodham Brook (Yeo (Somset)) | TRIBUTARY OF THE RIVER YEO |  |  |  |  | Commissioned in 2019 - full year data expected | 1 | 3 | 0 | 61 | 1154.4333 | 92.9304 | 16.25 | 4 (installed 2019) |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold |  | Stage 1a: Confirmed "exceptional weather" issue | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015600 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16707C | QUEEN CAMEL MILDMAY PLACE IN THE REAR GARDEN OF MILDMAY ORCHARD | 101773 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST5960225024 | GB108052015650 | Cam - Lower | RIVER CAM |  |  |  |  | Commissioned in 2018 - full year data expected | 9 | 7 | 7 | 21 | 89.0333 | 99.8158 | 10.8333 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015650 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16720S | CURRY RIVEL CURRY RIVEL STORM O/F | 082087 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST3971124606 | GB108052015470 | Parrett - R Yeo to West Sedgemoor Drain | TRIBUTARY OF DRAYTON DRAIN |  |  |  |  | Commissioned in 2019 - full year data expected | 10 | 6 | 8 | 9 | 91.75 | 99.9372 | 9 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015470 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16722C | WOTTON-UNDER-EDGE BRICKFIELDS | 102082 | SO on sewer network |  | Diluted | Rainwater | STROUD | The Cotswolds Co Const | ST7580992555 | GB109054026610 | Ozleworth Bk - source to conf Little Avon R | DYERS BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 99.6766 | 0 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026610 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16733C | TAUNTON MILL LANE CORFE NO 2 | 103193 | SO on sewer network |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST2344819649 | GB108052015420 | Broughton Brook (South and West Somerset) | TRIB OF BROUGHTON BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 5 | 9 | 13.8333 | 99.5529 | 7 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015420 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16738C | WELLINGTON RELYON FACTORY ENTRANCE | 013463 | SO on sewer network |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST1309022090 | GB108052015481 | Tone - Wellington to Taunton | RIVER TONE VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 2 | 2 | 3 | 2 | 1.1667 | 98.815 | 2.6667 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015481 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16749C | NORTH CURRY QUEENS SQUARE | 070910 | SO on sewer network |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST3130025880 | 200 | Not part of a river WB catchment | TRIB OF HAYMOOR OLD RHYNE SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 0 | 1 | 0 | 1 | 0.13333 | 99.9737 | 0.5 | 4 (installed 2019) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16750C | NORTH CURRY WINDMILL HILL | 102264 | SO on sewer network |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST3199925973 | 200 | Not part of a river WB catchment | TRIB OF HAYMOOR MAIN DRAIN SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 10 | 2 | 1 | 3 | 0.33333 | 99.9148 | 4 | 5 (installed 2018) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16766C | RADSTOCK WATERLOO ROAD SO (DOWNSTREAM) | EPRAP3921XS | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6950854967 | GB109053022271 | Wellow Bk - Snails Bk to Bristol Avon | THE WELLOW BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 2 | 0.66667 | 99.6781 | 1 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022271 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16770C | CAMERTON BRIDGE PLACE ROAD MH D19 | 013268 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6826157822 | GB109053022290 | Cam Bk - source to conf Wellow Bk | CAM BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 6 | 8 | 3 | 7 | 31.7333 | 99.9745 | 5.3333 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022290 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16772C | BATHEASTON BATHEASTON GARDEN | 100503/CS/01 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST7791267388 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 4 | 2 | 1 | 1 | 0.56667 | 95.3839 | 15 | 5 (installed 2018) | [5 empty] | 2020-11-30 | No sewage litter or sewage fungus | [6 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16784C | KEYNSHAM CHARLTON ROAD O/S 138 | 102127 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6472068950 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | CHARLTON BOTTOM VIA SWS |  |  |  |  | Commissioned in 2017 - full year data expected | 12 | 10 | 6 | 11 | 17.5 | 99.9921 | 7.8571 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16788C | MIDFORD ADJ ABANDONED RAILWAY | 100501/CS/01 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST7612860824 | GB109053022271 | Wellow Bk - Snails Bk to Bristol Avon | MIDFORD BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 8 | 2 | 2 | 3 | 1.3667 | 100 | 3.6 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022271 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16794C | FORDINGTON HIGH STREET NO 97 | 400682 | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | SY7005090550 | GB108044009691 | Frome Dorset (Lower) u/s Louds Mill Dorchester | (S) MILL STREAM |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 2 | 3 | 1 | 99.9797 | 1.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009691 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16798C | DORCHESTER PRINCES BRIDGE | 400684 | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | SY7001090590 | GB108044009691 | Frome Dorset (Lower) u/s Louds Mill Dorchester | (S) MILL STREAM |  |  |  |  | Commissioned in 2018 - full year data expected | 3 | 1 | 0 | 10 | 101.5 | 99.974 | 3.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009691 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16800C | DORCHESTER SOUTH WALKS / SOUTH STREET | 400688 | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | SY6954890767 | GB108044009691 | Frome Dorset (Lower) u/s Louds Mill Dorchester | RIVER FROME VIA SWS |  |  |  |  | Commissioned in 2021 - full year data expected |  | 0 | 0 | 0 | 0 | 99.9129 | 0 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009691 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16802C | DORCHESTER VICTORIA ROAD / DAMERS ROAD | EPRAP3920GG | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | SY6954890767 | GB108044009691 | Frome Dorset (Lower) u/s Louds Mill Dorchester | THE MILL STREAM VIA SWS |  |  |  |  | Commissioned in 2017 - full year data expected | 3 | 3 | 6 | 3 | 0.5 | 99.9049 | 4.1667 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009691 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16805C | SHERBORNE WESTBURY OPP DALWOODS | 070891 | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | ST6350015760 | GB108052015630 | Yeo | RIVER YEO VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 2 | 1 | 0.4 | 99.0841 | 1.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015630 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16806C | SHERBORNE LONG STREET OUTSIDE THORN BANK | 070885 | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | ST6408016250 | GB108052015630 | Yeo | RIVER YEO VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected |  | 1 | 3 | 1 | 0.36667 | 99.6796 | 1.6667 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015630 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16807C | SHERBORNE LUDBORNE ROAD / SOUTH STREET | NPSWQD002502 | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | ST6408016250 | GB108052015630 | Yeo | RIVER YEO VIA SWS |  |  |  |  | Commissioned in 2017 - full year data expected | 10 | 15 | 6 | 6 | 34.4667 | 91.1484 | 9.1667 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015630 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16808C | SHERBORNE NEWLANDS/THE AVENUE | 070887 | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | ST6419016335 | GB108052015630 | Yeo | RIVER YEO VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 5 | 15 | 11 | 11 | 3.1667 | 99.9562 | 9.2 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015630 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16810C | SHERBORNE LONG STREET THE VINES | 070886 | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | ST6418716334 | GB108052015630 | Yeo | RIVER YEO VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected |  | 1 | 3 | 1 | 0.2 | 99.911 | 1.6667 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015630 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16811C | BRIDPORT EAST BRIDGE | 402081 | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | SY4705492852 | GB108044009580 | Asker | RIVER ASKER(S) |  |  |  |  | Commissioned in 2020 - full year data expected |  | 3 | 3 | 4 | 5 | 99.9745 | 3.3333 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009580 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16817C | BURTON BRADSTOCK GROVE ROAD | 401868 | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | SY4894089630 | GB108044009550 | Bride | RIVER BRIDE(S) |  |  |  |  | Commissioned in 2018 - full year data expected | 4 | 6 | 4 | 10 | 41.3333 | 99.6591 | 6 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009550 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16819C | CHARMOUTH THE STREET ADJ BENHARH | 401594 | SO on sewer network |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | SY3679093690 | GB108044009770 | Monkton Wyld Stream | RIVER CHAR |  | CHARMOUTH WEST | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=charm&site=ukk2205-21300 |  | Commissioned in 2016 - full year data expected | 5 | 3 | 0 | 0 | 0 | 99.0892 | 1.75 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009770 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16827C | CLEVEDON PARNELL ROAD | 102296 | SO on sewer network |  | Diluted | Rainwater | NORTH SOMERSET | North Somerset Co Const | ST4098871164 | GB109052027321 | Land Yeo - Yearling Ditch to mouth | LAND YEO |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 92.6705 | 0 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052027321 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16852C | WEYMOUTH GRASMERE ROAD | 401285 | SO on sewer network |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6713480939 | GB108044010210 | Wey | RADIPOLE LAKE |  |  |  |  | Commissioned in 2017 - full year data expected | 1 | 4 | 0 | 3 | 1.9167 | 99.9254 | 3.6667 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010210 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16853C | WEYMOUTH LONGCROFT ROAD / QUEENSLAND ROAD | 400902 | SO on sewer network |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6758078730 | GB510804415700 | WEY | WEYMOUTH HARBOUR(E) | PORTLAND NORTH EASTERN BREAKWATER |  |  |  | Commissioned in 2016 - full year data expected | 9 | 5 | 2 | 7 | 0.7 | 57.2603 | 5.25 | 7 (installed 2016) | Sensor failure / issue | Resolved - Jun |  |  |  | 2023-10-05 | Sea outfall - N/A |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB510804415700 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16854C | WEYMOUTH MARLOW ROAD | 400895 | SO on sewer network |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6805978622 | GB510804415700 | WEY | WEYMOUTH HARBOUR VIA SWS (E) |  |  |  |  | Commissioned in 2019 - full year data expected | 0 | 1 | 1 | 3 | 0.75 | 100 | 1.5714 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB510804415700 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16862C | WEYMOUTH ULLSWATER CRESCENT | 401286 | SO on sewer network |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6721080970 | GB108044010210 | Wey | RADIPOLE LAKE VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 1 | 4 | 8 | 3 | 0.33333 | 99.7516 | 3 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010210 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16864C | WEYMOUTH WESTON ROAD | 400899 | SO on sewer network |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6758078730 | GB510804415700 | WEY | WEYMOUTH HARBOUR(E) | PORTLAND NORTH EASTERN BREAKWATER |  |  |  | Commissioned in 2020 - full year data expected | 0 | 3 | 2 | 3 | 2.0667 | 99.8954 | 1.2857 | 3 (installed 2020) | [5 empty] | 2023-10-05 | Sea outfall - N/A |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB510804415700 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16867B | PORTLAND RAILWAY GRAVITY SEWER | 040634 | Storm discharge at pumping station |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY7070072300 | GB620705550000 | Dorset / Hampshire | LYME BAY (C) |  |  |  |  | Commissioned in 2018 - full year data expected | 3 | 2 | 3 | 2 | 0.56667 | 99.9893 | 2.8 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620705550000 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16895C | MINEHEAD GREEN SPOT | 101775 | SO on sewer network |  | Diluted and partially treated | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | SS9727047320 | GB640807670000 | Bristol Channel Inner South | BRISTOL CHANNEL (C) |  | MINEHEAD TERMINUS | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=mineh&site=ukk2305-35000 |  | Commissioned in 2016 - full year data expected | 0 | 0 | 0 | 2 | 4.5833 | 99.9709 | 0.75 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB640807670000 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16901C | WESTBURY ALFRED ST CONSERVATIVE CLUB | 103574 | SO on sewer network |  | Diluted | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8743251549 | GB109053021770 | Bitham Bk - source to conf Biss Bk | BITHAM BROOK |  |  |  |  | Commissioned in 2017 - full year data expected | 3 | 2 | 2 | 4 | 0.6 | 99.9608 | 2.5 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021770 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16904C | WESTBURY WEST END O/S 36 | 103575 | SO on sewer network |  | Diluted | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8724851947 | GB109053021770 | Bitham Bk - source to conf Biss Bk | BITHAM BROOK VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 3 | 2 | 2 | 2 | 0.13333 | 95.2412 | 2.4 | 5 (installed 2018) | [12 empty] | Study in 2021 to assess the impact of Amesbury and Ratfyn WRCs. No separation of settled storm overflow and treated final effluent. Slight impact from Amesbury and slightly more from Ratfyn though apparent recovery within 1km. | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021770 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16922C | SAINT ALDHELMS BARTON BRIDGE BARTON FARM (175M DS) | 101648 | SO on sewer network |  | Diluted | Rainwater | WEST WILTSHIRE | Chippenham Co Const | ST8211260482 | GB109053027372 | Bristol Avon (Semington Bk to By Bk) | RIVER AVON |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 2 | 8 | 64.3333 | 99.9874 | 4.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027372 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16925C | BRADFORD-ON-AVON MARKET STREET/ SILVER STREET JUNCTION | 101651 | SO on sewer network |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | Chippenham Co Const | ST8263760963 | GB109053027372 | Bristol Avon (Semington Bk to By Bk) | RIVER AVON (VIA SWS) |  |  |  |  | Commissioned in 2018 - full year data expected | 13 | 10 | 9 | 19 | 120.1667 | 98.8706 | 8.4286 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027372 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16934C | TROWBRIDGE THE SHIRES MULTI-STOREY CAR PARK/BASEMENT | 101007 | SO on sewer network |  | Diluted | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8473058270 | GB109053021791 | Biss (Bitham Bk to Bristol Avon) | RIVER BISS VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 99.9357 | 0 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021791 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16935C | TROWBRIDGE STALLARD STREET O/S 58 | 101008 | SO on sewer network |  | Diluted | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8473258269 | GB109053021791 | Biss (Bitham Bk to Bristol Avon) | THE RIVER BISS VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 1 | 0 | 1 | 0.56667 | 99.941 | 0.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021791 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16938C | BURNHAM-ON-SEA ST ANDREWS SCHOOL LOVE LANE | 103857 | SO on sewer network |  | Diluted | Rainwater | SEDGEMOOR | Wells Co Const | ST3086049190 | 201 | Not part of a river WB catchment | A LOCAL DITCH |  | BURNHAM JETTY NORTH | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=burnh&site=ukk2302-35300 |  | Commissioned in 2018 - full year data expected | 0 | 4 | 3 | 1 | 1.0333 | 100 | 2.375 | 5 (installed 2018) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16944C | CLEEVE OLD CLEEVE FARM | 070950 | SO on sewer network |  | Diluted | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | ST0332042180 | GB108051020390 | Pill | PILL RIVER |  | BLUE ANCHOR WEST | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=blue%20a&site=ukk2305-35200 |  | Commissioned in 2019 - full year data expected | 0 | 0 | 2 | 1 | 0.96667 | 100 | 2.25 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108051020390 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16955C | YEOVIL PRESTON GROVE O/S 55 | EPRAP3922GF | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5463416018 | GB108052015600 | Dodham Brook (Yeo (Somset)) | A TRIBUTARY OF THE RIVER YEO |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 1 | 1 | 0.9 | 98.6514 | 1 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015600 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
16956C | YEOVIL HENFORD O/S HEALTH CENTRE | 103570 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5530915447 | GB108052015600 | Dodham Brook (Yeo (Somset)) | DODHAM BROOK VIA SWS |  |  |  |  | Commissioned in 2021 - full year data expected |  | 7 | 7 | 7 | 0.73333 | 99.9231 | 7 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015600 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17029C | PORTLAND WESTON STREET NEW | 401192 | SO on sewer network |  | Diluted and partially treated | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6851470883 | 2 | Not part of a river WB catchment | GROUNDWATER VIA INFILT SYSTEM |  |  |  |  | Commissioned in 2018 - full year data expected | 5 | 9 | 8 | 12 | 7.3667 | 97.266 | 8.5 | 5 (installed 2018) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17062S | RINGSTEAD RINGSTEAD BAY STORM TANK | 401738 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | WEST DORSET | South Dorset Co Const | SY7516781575 | 250 | Not part of a river WB catchment | UNNAMED STREAM(S) |  | RINGSTEAD BAY | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=ringst&site=ukk2206-20300 |  | Commissioned in 2016 - full year data expected | 1 | 0 | 0 | 3 | 16.0833 | 96.7258 | 3.875 | 7 (installed 2016) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17123C | BRISTOL EASTVILLE PARK FISHPONDS BROOK | 100457 | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol East Boro Const | ST6183675667 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | RIVER FROME |  |  |  |  | Commissioned in 2016 - full year data expected | 3 | 7 | 1 | 9 | 24.3306 | 100 | 5.125 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17175B | PURITON DOWNEND TERRACE | 102773 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | SEDGEMOOR | Bridgwater and West Somerset Co Const | ST3116041430 | 200 | Not part of a river WB catchment | UN-NAMED DITCH (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 1 | 3 | 4 | 99.9286 | 1 | 5 (installed 2018) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17258S | MONKTON DEVERILL HINDON ROAD STORM TANK | 401861 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | WEST WILTSHIRE | South West Wiltshire Co Const | ST8541637249 | GB108043022520 | Wylye (Headwaters) | RIVER WYLYE |  |  |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 0 | 0 | 0 | 81.464 | 0 | 4 (installed 2019) | Telemetry or data archiving failure / issue | Scheduled | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022520 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17318C | TAUNTON BRIDGWATER ROAD O/S 75 | 070906 | SO on sewer network |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST2482025257 | GB108052015482 | Tone Ds Taunton | TRIBUTARY OF THE RIVER TONE |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 1 | 2 | 1 | 0.066667 | 89.5586 | 1 | 5 (installed 2018) | Sensor failure / issue | Resolved - Mar | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015482 | Yes |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17350C | RADSTOCK WATERLOO ROAD BUILDERS YARD | 103351 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6904454862 | GB109053022250 | Wellow Bk - source to conf Snails Bk | WELLOW BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 1 | 0 | 1 | 0.033333 | 80.1739 | 0.5 | 5 (installed 2018) | Sensor failure / issue | Resolved - Mar | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022250 | Yes |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17356C | BISHOPS LYDEARD CHURCH STREET | 103195 | SO on sewer network |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST1717129627 | GB108052021390 | Back Stream | TRIB OF THE BACK STREAM |  |  |  |  | Commissioned in 2020 - full year data expected |  | 3 | 4 | 3 | 2.1667 | 99.9254 | 3.3333 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021390 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17370C | TAUNTON WILTON ORCHARD CAR PARK | EPRJB3797AQ | SO on sewer network |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST2253024007 | GB108052015410 | Sherford Stream | GAOL STREAM VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 0 | 0 | 99.9779 | 0 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015410 | Yes |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17375S | HOLT POND HEAD STORM TANK | 402465 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | EAST DORSET | North Dorset Co Const | SU0339004570 | GB108043011080 | Uddens Water | TRIBUTARY OF UDDENS WATER |  |  |  |  | Commissioned in 2020 - full year data expected |  | 7 | 9 | 16 | 58.1333 | 100 | 10.6667 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011080 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17378C | STOGURSEY CHURCH ST NR 5-7 | EPRAP3829XV | SO on sewer network |  | Diluted | Rainwater | WEST SOMERSET | Bridgwater and West Somerset Co Const | ST2044442881 | GB108052021340 | Stogursey BK | STOGURSEY BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 8 | 9 | 6 | 8 | 10.1333 | 99.7546 | 8.8333 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021340 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17383C | TAUNTON STOKE ROAD O/S 15 | EPRJB3798VJ | SO on sewer network |  | Diluted | Rainwater | TAUNTON DEANE | Taunton Deane Co Const | ST2391723478 | GB108052015420 | Broughton Brook (South and West Somerset) | BLACK BROOK |  |  |  |  | Commissioned in 2020 - full year data expected | 0 | 11 | 5 | 2 | 1.2 | 99.6495 | 4.5 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015420 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17385C | BRISTOL LINDEN ROAD JNC HOWARD ROAD | NPSWQD010513 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5861075072 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | CRANBROOK VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected |  | 6 | 4 | 3 | 0.4 | 99.9799 | 4.3333 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17386C | BRISTOL HOLLYGUEST ROAD JNC GREENBANK ROAD | Unpermitted | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6289572185 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | Bristol Avon (By Bk to Netham Weir) |  |  |  |  | Aug 2023 |  |  |  | 0 | 0 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17388C | BRISTOL HOLLYGUEST ROAD R/O 21 | Unpermitted | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6289572185 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | Bristol Avon (By Bk to Netham Weir) |  |  |  |  | Aug 2023 |  |  |  | 1 | 0.3 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17389C | BRISTOL HOLLYGUEST ROAD O/S 16 | Unpermitted | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6289572185 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | Bristol Avon (By Bk to Netham Weir) |  |  |  |  | Aug 2023 |  |  |  | 1 | 0.26667 | 100 |  | <1 yr (installed 2023) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17392C | RADSTOCK WALEGRAVE TERRACE OPP 9 | EPRAP3922XM | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST6950854967 | GB109053022271 | Wellow Bk - Snails Bk to Bristol Avon | WELLOW BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 99.516 | 0 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022271 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17396C | BRIDPORT WEST BAY ROAD REAR GARDEN OF 13A | 041198 | SO on sewer network |  | Diluted | Rainwater | WEST DORSET | West Dorset Co Const | SY4635191351 | GB108044009540 | Brit (Lower) | RIVER BRIT |  |  |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 1 | 0 | 0 | 100 | 0.25 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009540 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17430S | GAUNTS COMMON STORM TANK | 402509 | Storm tank at WwTW |  | Diluted and partially treated | Rainwater | EAST DORSET | North Dorset Co Const | SU0260004920 | GB108043011080 | Uddens Water | TRIBUTARY OF UDDENS WATER |  |  |  |  | Commissioned in 2020 - full year data expected |  | 0 | 0 | 4 | 24.7 | 98.9916 | 1.3333 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011080 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17447C | BRISTOL CAIRNS ROAD O/S 42 | NPSWQD010511 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5861075072 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | CRANBROOK |  |  |  |  | Commissioned in 2019 - full year data expected | 3 | 9 | 8 | 3 | 0.25 | 100 | 5.75 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17485C | CHRISTIAN MALFORD CHURCH ROAD | NPSWQD001988 | Storm discharge at pumping station |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9616078820 | GB109053027650 | Avon (Brist) conf Tetbury Avon to conf R Marden | A TRIBUTARY OF THE RIVER AVON |  |  |  |  | Commissioned in 2017 - full year data expected | 0 | 1 | 0 | 1 | 2.0958 | 100 | 0.5 | 6 (installed 2017) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027650 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17510C | BATH BRASSMILL LANE O/S NO 62 | NPSWQD010268 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7215565110 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | RIVER AVON (VIA SWS) |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 95.7785 | 0.125 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17537C | BATH FAIRFIELD AVENUE R/O NO 30 | 103856 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7625066580 | GB109053022300 | Lam Bk - source to conf R Avon (Brist) | LAM BROOK VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 2 | 4 | 0 | 0 | 99.9224 | 1.8333 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022300 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17538C | BATH BAYTREE ROAD ALLOTMENTS R/O NO 28 | 103603 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7625066580 | GB109053022300 | Lam Bk - source to conf R Avon (Brist) | LAM BROOK VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 20 | 8 | 9 | 11 | 0.8 | 99.9996 | 8.3333 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022300 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17542C | BATH CAR PARK ADJ J HUGHES COTTAGE | 103903 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7624366614 | GB109053022300 | Lam Bk - source to conf R Avon (Brist) | LAM BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 20 | 5 | 5 | 16 | 47.5667 | 100 | 10 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022300 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17552C | WESTON-SUPER-MARE GREENFIELD PLACE O/S 15 | Unpermitted | SO on sewer network |  | Diluted | Rainwater | NORTH SOMERSET | Weston-Super-Mare Co Const | ST3145161883 | GB640807670000 | Bristol Channel Inner South | Bristol Channel Inner South |  | WESTON-SUPER-MARE UPHILL SLIPWAY/WESTON MAIN |  |  | Commissioned in 2020 - full year data expected |  |  |  | 0 | 0 | 87.1233 | 0 | 3 (installed 2020) | Telemetry or data archiving failure / issue | Resolved - Feb | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB540805210900 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17577C | BRISTOL HOWARD RD JNC FALLODON WY/HALSBURY RD | NPSWQD010512 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5861175071 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | CRANBROOK |  |  |  |  | Commissioned in 2020 - full year data expected |  | 7 | 3 | 3 | 0.4 | 99.7858 | 4.3333 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
17589C | BATH DARTMOUTH AVE NR ENTRANCE TO LINEAR PARK | NPSWQD010267 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | Bath Boro Const | ST7340864926 | GB109053027371 | Bristol Avon (By Bk to Netham Weir) | THE RIVER AVON VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 95.583 | 0 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027371 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
14395B | HATCH BEAUCHAMP | 070916 | Storm discharge at pumping station |  | Diluted | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST3064520034 | GB108052015241 | Fivehead River | TRIBUTARY OF FIVEHEAD RIVER |  |  |  |  | Commissioned in 2021 - full year data expected | 6 |  | 6 | 18 | 75.8333 | 90.3954 | 10 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015241 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
15310B | ALLER | 071143 | Storm discharge at pumping station |  | Diluted | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST3974229206 | GB108052021150 | King's Sedgemoor Drain - Henley Sluice to mouth | OXLEASEDROVE RHYNE EAST |  |  |  |  | Commissioned in 2018 - full year data expected | 7 |  | 8 | 15 | 68.3667 | 100 | 10 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021150 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19050C | CAM VALLEY SPLOT FARM NR PEASEDOWN ST JOHN | 013266 | SO on sewer network |  | Diluted | Rainwater | BATH AND NORTH-EAST SOMERSET | North East Somerset Co Const | ST7014758586 | GB109053022290 | Cam Bk - source to conf Wellow Bk | TRIB OF CAM BROOK |  |  |  |  | Commissioned in 2018 - full year data expected | 3 | 2 | 0 | 0 | 0 | 99.9376 | 1.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022290 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19056B | WEYMOUTH CASTLE COVE OLD CASTLE ROAD WYKE REGIS | EPRAP3923KW | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6768477538 | GB680805270000 | Portland Harbour | PORTLAND HARBOUR | PORTLAND NORTH EASTERN BREAKWATER | PORTLAND HARBOUR CASTLE COVE/PORTLAND HARBOUR SANDSFOOT CASTLE | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=castle%20co&site=ukk2206-20800 | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=sandsf&site=ukk2206-20900 | Commissioned in 2016 - full year data expected | 2 | 1 | 1 | 5 | 4.1525 | 99.9998 | 1.5 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB680805270000 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19123C | PORTISHEAD BRAMPTON WAY | 100556/CS/01 | SO on sewer network |  | Diluted | Rainwater | NORTH SOMERSET | North Somerset Co Const | ST4707076150 | GB109052027330 | Portbury Ditch - source to conf R Severn Estuary | PORTBURY DITCH VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 1 | 1 | 0 | 0 | 0 | 99.5419 | 2.6 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052027330 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19173C | STOKE GIFFORD NEW ROAD ALONG SIDE NO 177 | 101681 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Filton and Bradley Stoke Co Const | ST6187380229 | GB109053027540 | Stoke Bk - source to conf Bradley Bk | TRIB OF STOKE BROOK VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 0 | 0 | 86.8775 | 0 | 3 (installed 2020) | Sensor failure / issue | Resolved - Dec | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027540 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19252C | BRISTOL KINGSWOOD DOWNLEAZE ROAD R/O 14 | 101643 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Filton and Bradley Stoke Co Const | ST6495378410 | GB109053027820 | Frome (Brist) - conf Laddon Bk to conf Folly Bk | TRIB OF RIVER FROME VIA SWS |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 99.8242 | 0 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027820 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19258C | BRISTOL BATH ROAD JUNCTION FLOWERS HILL | 100581/CS/01 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol East Boro Const | ST6199270650 | GB109053021980 | Brislington Bk - source to conf R Avon (Brist) | BRISLINGTON BROOK VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 0 | 0 | 0 | 90.8368 | 0 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021980 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19266C | BOURNEMOUTH FISHERMANS WALK CIS | 051310 | SO on sewer network |  | Diluted and partially treated | Rainwater | BOURNEMOUTH | Bournemouth East Boro Const | SZ1287490694 | GB620705550000 | Dorset / Hampshire | ENGLISH CHANNEL | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA | BOURNEMOUTH FISHERMAN'S WALK | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=bournem&site=ukk2101-19030 |  | Commissioned in 2018 - full year data expected | 0 | 2 | 0 | 1 | 1.0333 | 96.9117 | 0.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620705550000 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19275C | OLVESTON GREEN FARM OPP LOWER LEAZE | 101836 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6003886841 | GB109054026650 | Chestle Pill | TRIB. OF OLVESTON MILL RHINE |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 1 | 0.7 | 99.8965 | 0.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026650 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19281C | BRISTOL HENLEAZE PARK DRIVE JUNCTION OAKWOOD ROAD | 100458 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5801977358 | GB109053027530 | Trym - source to conf R Avon (Brist) | TRIB OF RIVER TRYM VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 1 | 1 | 0 | 0 | 91.2591 | 0.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027530 | Yes |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19307C | BRISTOL KINGSWOOD SOUTHEY PLAYING FIELDS (NEW CHELTENHAM ROAD ADJ NO 84) | 100891 | SO on sewer network |  | Diluted and partially treated | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6631974374 | GB109053027450 | Siston Bk - source to conf R Avon (Brist) | WARMLEY BROOK(S) |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 0 | 0 | 0 | 99.7131 | 0 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027450 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19467C | WOOKEY AXE ROAD O/S RIVERSIDE COTTAGE | 102492 | SO on sewer network |  | Diluted | Rainwater | MENDIP | Wells Co Const | ST5149545623 | GB109052021520 | Axe - source to Cocklake | RIVER AXE |  |  |  |  | Commissioned in 2018 - full year data expected | 2 | 1 | 4 | 4 | 14.3 | 99.5784 | 1.5 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109052021520 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19529C | POOLE POOLE PARK ATTENUATION TANK | 400457 | SO on sewer network |  | Diluted and partially treated | Rainwater | POOLE | Poole Boro Const | SZ0252890989 | 68 | Not part of a river WB catchment | POOLE PARK BOATING LAKE | POOLE HARBOUR BRANDS BAY / POOLE HARBOUR NORTH / ROCKLEY / SW BROWNSEA ISLAND / WAREHAM CHANNEL / WHITLEY LAKE / WYCH LAKE / NORTH HAVEN PONTOON / LYCHETT BAY / SOUTH DEEP / WEST BROWNSEA RELAY AREA |  |  |  | Commissioned in 2016 - full year data expected | 5 | 4 | 3 | 4 | 17.6403 | 98.6252 | 3.625 | 7 (installed 2016) | [13 empty] | Not part of a river WB catchment | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19534C | WEYMOUTH CHICKERELL ROAD O/S ALLOTMENTS NEAR THE ADMIRAL HARDY | 400903 | SO on sewer network |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6758078730 | GB510804415700 | WEY | WEYMOUTH HARBOUR(E) | PORTLAND NORTH EASTERN BREAKWATER | WEYMOUTH CENTRAL | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=weymouth&site=ukk2206-20700 |  | Commissioned in 2019 - full year data expected | 8 | 4 | 6 | 8 | 24.3667 | 99.7496 | 9.25 | 4 (installed 2019) | [5 empty] | 2023-10-05 | Sea outfall - N/A |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB510804415700 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19541A | SWANAGE MARINE PARADE 1 | 400785 | SO on sewer network |  | Diluted | Rainwater | PURBECK | South Dorset Co Const | SZ0424378665 | GB620705550000 | Dorset / Hampshire | SWANAGE BAY |  | SWANAGE CENTRAL | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=swanage&site=ukk2204-19800 |  | Commissioned in 2016 - full year data expected | 1 | 1 | 0 | 3 | 4.5333 | 98.0563 | 2.125 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620705550000 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19541B | SWANAGE MARINE PARADE 2 | 400785 | SO on sewer network |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SZ0424378665 | GB620705550000 | Dorset / Hampshire | SWANAGE BAY |  | SWANAGE CENTRAL | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=swanage&site=ukk2204-19800 |  | Commissioned in 2018 - full year data expected | 1 | 1 | 0 | 3 | 4.5333 | 99.7549 | 1 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620705550000 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19553C | BOURNEMOUTH ASHLEY ROAD JNC WILSON ROAD | 042745 | SO on sewer network |  | Diluted | Rainwater | BOURNEMOUTH | Bournemouth East Boro Const | SZ1313393813 | GB108043011040 | Stour (Lower) | TRIB OF RIVER STOUR(S) |  |  |  |  | Commissioned in 2020 - full year data expected |  | 4 | 2 | 3 | 0.23333 | 99.8664 | 3 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043011040 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19557C | WEYMOUTH SPRING ROAD NR JUNC WITH MOUNT STREET | 400900 | SO on sewer network |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6806078620 | GB510804415700 | WEY | WEYMOUTH HARBOUR(E) - COVE ROW | PORTLAND NORTH EASTERN BREAKWATER |  |  |  | Commissioned in 2016 - full year data expected | 0 | 0 | 1 | 2 | 0.21194 | 99.5488 | 0.625 | 7 (installed 2016) | [5 empty] | 2023-10-05 | Sea outfall - fungus spotted at the outfall |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB510804415700 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19560C | BRISTOL STATION ROAD R/O 198 CHELTENHAM ROAD (CUTTERS MILLS CULVERT) | 100877 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol West Boro Const | ST5616074420 | GB530905415405 | BRISTOL AVON | RIVER AVON |  |  |  |  | Commissioned in 2019 - full year data expected | 0 | 6 | 1 | 1 | 0.16667 | 100 | 1.8 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19575C | MUDFORD TRENT VIEW IN F/G (A359) | 071726 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST5718619241 | GB108052015682 | Yeo Ds Over Compton | TRIBUTARY OF THE RIVER YEO |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 1 | 0 | 0 | 0 | 99.9829 | 0.25 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015682 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19577C | SOUTH PETHERTON WEST ST O/S 12 | 102764 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Yeovil Co Const | ST4320716579 | GB108052015340 | Lam Brook | TRIB OF NORTH MILL BROOK |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 0 | 0 | 0 | 98.3116 | 0 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015340 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19578C | SOMERTON NEW HILL NR 16 | 103571 | SO on sewer network |  | Diluted | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST4956028760 | GB108052015140 | Cary - source to conf with KSD | TRIBUTARY OF RIVER CARY |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 1 | 0 | 0 | 100 | 0.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015140 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19670C | BRISTOL COOMBE BROOK TANK RIDGEWAY PLAYING FIELDS NR VERA ROAD | 101644 | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol East Boro Const | ST6233074960 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | COOMBE BROOK VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 5 | 4 | 1 | 2 | 0.75 | 100 | 3.6667 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19674C | TOCKINGTON LOWER TOCKINGTON ROAD ADJ TO IVYWELL | 101835 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Thornbury and Yate Co Const | ST6087886240 | GB109054026650 | Chestle Pill | TOCKINGTON MILL RHYNE |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 4 | 42 | 400.6333 | 99.8109 | 23 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109054026650 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19727C | WEYMOUTH KNIGHTSDALE ROAD ATTENUATION TANK | 400904 | SO on sewer network |  | Diluted and partially treated | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6758078730 | GB510804415700 | WEY | WEYMOUTH HARBOUR(E) | PORTLAND NORTH EASTERN BREAKWATER | WEYMOUTH CENTRAL | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=weymouth&site=ukk2206-20700 |  | Commissioned in 2016 - full year data expected | 7 | 5 | 6 | 9 | 24.4 | 96.0812 | 6.875 | 7 (installed 2016) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB510804415700 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19769C | BRISTOL CLEVE COURT FILTON | 101680 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Filton and Bradley Stoke Co Const | ST6074079980 | GB109053027540 | Stoke Bk - source to conf Bradley Bk | STOKE BROOK (S) |  |  |  |  | Commissioned in 2018 - full year data expected | 6 | 8 | 1 | 1 | 0.083333 | 100 | 4 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027540 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19770C | BRISTOL KINGSWOOD KINGSHOLME ROAD NO 86 | 100890 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Kingswood Boro Const | ST6631974374 | GB109053027450 | Siston Bk - source to conf R Avon (Brist) | WARMLEY BROOK VIA SWS |  |  |  |  | Commissioned in 2021 - full year data expected |  |  | 1 | 0 | 0 | 99.8512 | 0.5 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027450 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19780C | BRISTOL AMENITY LAND OPP NO.63 QUAKERS ROAD | 101434 | SO on sewer network |  | Diluted | Rainwater | SOUTH GLOUCESTERSHIRE | Filton and Bradley Stoke Co Const | ST6495078410 | GB109053027820 | Frome (Brist) - conf Laddon Bk to conf Folly Bk | TRIB OF STOCKWELL VIA SWS |  |  |  |  | Commissioned in 2020 - full year data expected | 1 | 1 | 1 | 0 | 0 | 95.0202 | 0.75 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027820 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19784C | WEYMOUTH CORONATION CRES 0/S NO.3 | 401287 | SO on sewer network |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6721080970 | GB108044010210 | Wey | RADIPOLE LAKE VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 1 | 5 | 10 | 11 | 2.5833 | 99.9905 | 4.8333 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010210 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19787B | STOUR ROW | 401115 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | NORTH DORSET | North Dorset Co Const | ST8207020790 | GB108043016100 | Key Brook | KEY BROOK(S) |  |  |  |  | Commissioned in 2020 - full year data expected |  | 5 | 14 | 10 | 62.5667 | 99.9909 | 9.6667 | 3 (installed 2020) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043016100 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19792C | WEYMOUTH SPA ROAD/ ROMAN ROAD AND QUEENS ROAD JCT. | 401288 | SO on sewer network |  | Diluted | Rainwater | WEYMOUTH AND PORTLAND | South Dorset Co Const | SY6721080970 | GB108044010210 | Wey | RADIPOLE LAKE VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 0 | 0 | 0 | 0 | 0 | 100 | 0.16667 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010210 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19817B | SANDFORD ORCAS | 102522 | Storm discharge at pumping station |  | Diluted and partially treated | Rainwater | WEST DORSET | West Dorset Co Const | ST6218421095 | GB108052015620 | Corton Denham Stream | CORTON DENHAM STREAM |  |  |  |  | Commissioned in 2019 - full year data expected | 1 | 0 | 0 | 4 | 22.1667 | 99.9772 | 1.2 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052015620 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19822C | SHAFTESBURY NEW ROAD/ WOOLANDS LANE | 401299 | SO on sewer network |  | Diluted | Rainwater | NORTH DORSET | North Dorset Co Const | ST8575723374 | GB108043022440 | Lodden | TRIBUTARY OF FERN BROOK |  |  |  |  | Commissioned in 2021 - full year data expected |  | 6 | 2 | 1 | 0.36667 | 99.3858 | 3 | 2 (installed 2021) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108043022440 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19837C | ALFORD INLET | 101966 | Inlet SO at WwTW |  | Diluted and partially treated | Rainwater | SOUTH SOMERSET | Somerton and Frome Co Const | ST6047532364 | GB108052021183 | Brue - R. Alham to Tootle Bridge | TRIBUTARY OF RIVER BRUE |  |  |  |  | Commissioned in 2018 - full year data expected | 2 | 0 | 13 | 32 | 249.9 | 99.6747 | 11.75 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108052021183 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19883C | MALMESBURY GLOUCESTER ROAD O/S 109 | 102682 | SO on sewer network |  | Diluted | Rainwater | NORTH WILTSHIRE | North Wiltshire Co Const | ST9307187758 | GB109053027780 | Tetbury Avon - unnamed trib to conf Sherston Avon | RIVER AVON (TETBURY BRANCH) |  |  |  |  | Commissioned in 2018 - full year data expected | 11 | 10 | 6 | 21 | 9.4333 | 99.7546 | 10.8333 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027780 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19885C | AVONMOUTH LOWER HIGH STREET O/S NO. 27 | 102066 | SO on sewer network |  | Diluted | Rainwater | BRISTOL | Bristol North West Boro Const | ST5202077010 | GB530905415405 | BRISTOL AVON | RIVER AVON VIA SWS (ESTUARINE) |  |  |  |  | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 0 | 0 | 78.2078 | 0.33333 | 5 (installed 2018) | Telemetry or data archiving failure / issue | Resolved - Mar | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB530905415405 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19928C | BRISTOL QUEENS HEAD PUB QUEENS ROAD RETENTION TANK | 101824 | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol South Boro Const | ST5701268181 | GB109053021970 | The Malago - source to conf R Avon (Brist New Cut) | MALAGO |  |  |  |  | Commissioned in 2022 - full year data expected |  |  | 5 | 8 | 41.3333 | 99.882 | 6.5 | 1 (installed 2022) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053021970 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19947C | SWANAGE HERSTON CROSS ATTENUATION TANK | 402255 | SO on sewer network |  | Diluted and partially treated | Rainwater | PURBECK | South Dorset Co Const | SZ0173079090 | GB108044009920 | Swan (Swanage) | TRIB OF RIVER SWAN(S) |  | SWANAGE CENTRAL | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=swanage&site=ukk2204-19800 |  | Commissioned in 2016 - full year data expected | 2 | 3 | 2 | 5 | 7.2 | 87.664 | 3.25 | 7 (installed 2016) | Sensor failure / issue | Resolved - Feb | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009920 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19960C | BRISTOL SHEPPARD ROAD INTERCEPTOR | EPRNB3334AG | SO on sewer network |  | Diluted and partially treated | Rainwater | BRISTOL | Bristol East Boro Const | ST6383876803 | GB109053027840 | Frome (Brist) - Bradley Bk to conf Floating Hbr | TRIB OF RIVER FROME VIA SWS |  |  |  |  | Commissioned in 2019 - full year data expected | 2 | 4 | 1 | 1 | 0.75 | 100 | 1.6 | 4 (installed 2019) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053027840 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)
19984C | WEST LAVINGTON CHURCHILL ARMS NEW | 101815 | SO on sewer network |  | Diluted | Rainwater | KENNET | Devizes Co Const | SU0071353439 | GB109053022130 | Semington Bk - source to conf Worton Str | SEMINGTON BROOK VIA SWS |  |  |  |  | Commissioned in 2018 - full year data expected | 9 | 7 | 10 | 14 | 2.3333 | 96.9136 | 10 | 5 (installed 2018) | [13 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB109053022130 | No |  |  | 2023 or before | Already meets Storm Overflow Discharge Reduction Plan targets (see: https://www.gov.uk/government/publications/storm-overflows-discharge-reduction-plan)

## Warleigh Weir AI
Case Study - Warleigh Weir real time water quality monitoring for recreational users
We have been working with the landowner, the Rivers Trust, Bristol Avon Rivers Trust and the Environment Agency to discuss river water quality at the location, which can be affected by a number of factors – from our storm overflows and treated wastewater from our water recycling centres being returned to the river upstream to agricultural run-off, septic tanks, road drains and wild animals.
To understand more about water quality at this location, investigative work is underway to find out more about the factors in the large river catchment upstream of the site which influence the condition of the river water and the role our assets have. This work involves collecting water quality information and river flow and weather data from Warleigh Weir and the catchment upstream, as well as trialling real-time water quality monitoring sensors in the river. | Warleigh Weir Investigation
Real-time bacteria monitoring trial | Warleigh Weir water quality data
The quality of bathing waters is measured by looking at the concentration of faecal indicator bacteria present in them. There is currently no technology that can continuously measure the concentration of these bacteria in rivers, which means we can’t provide people with this information in real time. Instead, samples have to be collected by hand and taken to a laboratory where the bacteria are analysed under controlled conditions, which takes around three days.
However, there are many readily available sensors that can provide robust real-time measurements of other water quality indicators, including temperature, pH, conductivity, dissolved oxygen and river flow. We are working with UnifAI, a company specialising in the use of artificial intelligence (AI) technology, to trial an approach that uses algorithms to develop relationships between these readily measurable parameters and the concentration of bacteria in water. We are also trialling the limited range of sensors currently on the market which measure bacteria to test their accuracy, usability and application.
The diagram below illustrates the data sets being used by the AI platform to 'learn' the relationships and enable the proxy bacterial water quality to be shared in real time
The trial, which has been running since 2021, and has involved installing a variety of sensors, collecting water samples and analysing bacteria in the laboratory. As data has been collected the AI platform has learnt about these relationships and is now able to predict the bacterial water quality with >90% accuarcy. This has meant that, working with UnifAI Technology, we have been able to develop a webapp, available on smart phones, to provide recreational users with real time information about water quality, river flow and temperature. This enables swimmers to make informed decisions before getting into the water. The webapp is available for all to use.
Other Real Time Water Quality Projects
During 2023 we are working on a number of similar projects, working with stakeholders to provide real time information on water quality and recreational conditions. One of these projects is in Poole Harbour where we are working with the shellfishery and recreational sectors, in addition to academia, to develop a water quality forecasting system, similar to a weather forecast. This will provide a 6-hour forecast of the Norovirus and EColi concentrations across the Harbour, enabling users to plan their activities. We are also working with local authorities in other locations to install sensors and provide real time information at popular swimming or recreational spots, including Bristol Floating Harbour and elsewhere along the River Avon, and at Boscombe Pier.
We will report back on all of these projects more fully at the end of 2023

## Shrewton Case Study
Case Study - Shrewton WRC SSO
Shrewton WRC overflow operation
This case study has been updated to describe the changes made on site to treat the stormwater flows through a reedbed.
Wessex Water has reported EDM data for Shrewton to the Environment Agency illustrating both the frequency and duration of the overflow operation. These durations, whilst still prolonged, are not consistent with data quoted in the media in recent months.
The village of Shrewton is impacted by high groundwater levels at certain times of year, particularly over the winter months and into the late spring, typically between January and June each year. Wessex Water has responsibility for the public sewerage network and not the private drains from individual properties which connect into the public sewer. The length of private pipework far outweighs the length of public pipework and so represents a significant entry point for groundwater into the combined sewerage network which serves the village. Whilst Wessex Water has relined and sealed long lengths of our network to reduce this groundwater infiltration, we do not have the power to seal private pipes.
There is very little recorded surface water sewerage in Shrewton. It is limited to one cul-de-sac of 22 properties and it discharges to the adjacent River Till. There are two limited areas of recorded highway drainage. One discharges to the River Till, the other is a cul-de-sac of 7 houses off Chalk Hill. The remainder of the village is served by a combined system, including foul sewage from properties and rainwater from roofs, guttering and hardstanding throughout the village.
Figures 2 and 3 illustrate the extent of the Wessex Water sewerage network within the village. The red lines indicate the public sewerage network, private drains connecting individual properties to the public network are unmapped and the homeowners responsibility.
Extensive efforts were made to reduce infiltration in the catchment prior to 2008 but were unsuccessful. A new rising main (pumped sewer) was laid to the WRC where flows are screened before passing to a storm tank. There had been no storm storage or overflow at the works prior to this.
This area is currently being investigated as part of Wessex Water’s regional Infiltration Reduction Programme, as high risk of foul sewer inundation. Work so far has involved undertaking sewer surveys to identify points of groundwater ingress, followed by sewer sealing to address the defects. To date we have sealed 261m of public sewer in 2016-17, 134m in 2017-18, 121m in 2018-19 and 207m in 2019-20. Alongside this we have also sealed 33 manhole chambers to address groundwater ingress identified in those. Monitoring of the catchment is ongoing with infiltration still a major issue which also impacts on the WRC.
During survey work carried out in February 2022 we identified a substantial number of infiltration defects, which we have been working to resolve. 235m of public sewer has been relined this financial year (2022/23), with a further 550m to be delivered financial year 2023/24. 7 manhole chambers are also due to be renovated to stop infiltration.
The underlying geology for Shrewton is Seaford Chalk formation. Chalk is good for soakaways and aquifer properties as it is porous with lots of cracks in for water to pass through. This means it is a good store for groundwater and will drain surface water quickly, reducing storm response. However, once the aquifer is saturated, the water table rises and can cause groundwater flooding. Groundwater moves slowly so it can take a while for the level to rise sufficiently to have an impact on the sewer system. Once it has risen it then often takes a longer time to drain back down. These characteristics are present in Shrewton – ordinarily there is little storm response in the catchment, but during the winter months, the aquifer recharges over several months and then then stays high for several months, as illustrated below.
Historical rainfall has also been reviewed against spill activity to assess the relationship between spill activity, rainfall and infiltration:
• Spill activity is almost entirely associated with high infiltration between January and, at the latest, August
• The majority are long duration events in the first 6 months of the year
• For 2013, 2014, 2016, and 2018 there is almost continuous spilling from January through to June/July.
• Outside the infiltration season, the records show that storm spills from the Settled Storm Overflow (SSO) are extremely rare
The graph below shows the direct relationship between the groundwater level recorded at an observation borehole nearby (Tilshead) and the flow recorded at the inlet flow meter. This shows that when the groundwater level is higher than 82mAOD, the flow to the water recycling centre rapidly increases from less than 500m3/day to between 2 - 3,000m3/d. The graphs to the right show this in more detail between 2017 and 2020. Once the groundwater level rises above this level, 12 to 17 days later the flow at the water recycling centre dramatically increases. The water table is rising above the public (Wessex Water) and private (homeowner) sewerage system, infiltrating in to the pipes and causing a significantly greater flow of clean groundwater to mix with the foul and enter the water recycling centre.
Ecological impact of Shrewton WRC
We take samples up and downstream of all storm overflows of concern, for example those located within SSSIs. As the discharges are intermittent the invertebrate community can detect an impact that may be missed by water quality samples, since these samples cannot always be taken when the discharge is occurring due to access or health and safety concerns.
We measure outfall impact by taking invertebrate kick samples in spring and autumn up- and downstream of the outfall and comparing the number of taxa (NTAXA), a measure of diversity, and the average score per taxa (ASPT), a measure of the sample’s sensitivity to organic pollution. If either of these indices shows a significant decline in the downstream sample then the outfall is considered to cause a problem.
Ecological impact of Shrewton WRC
The results from Shrewton WRC sampled in 2017/18 are shown below:
|  | NTAXA |  | ASPT
|  | Upstream | Downstream | Upstream | Downstream
SHREWTON WRC 13275 | Autumn 2017 | 8 | 6 | 3.22 | 4.23
| Spring 2018 | 10 | 9 | 4.1 | 4.2
Table 2: Aquatic ecology survey data collected upstream and downstream of the final effluent and storm overflow discharge.
The results show a slight decline in NTAXA and increase in ASPT in both seasons sampled indicating no significant impact from the final effluent or settled storm overflow. The settled storm overflow at Shrewton discharges at the same point as the final effluent so it is not possible to separate the two effects.
Shrewton WRC discharges to the winterbourne section of the River Till. The aerial image below shows that the outfall creates a ponded reach for about 100m in an otherwise dry riverbed during the late summer/autumn.
Unfortunately, the impact of the discharge is complicated at winterbourne sites as there is not always any upstream flow. This means that the downstream sample is taken from undiluted final effluent and the upstream sample either cannot be taken or is actually the final effluent backing upstream as the outfall is in a ponded low gradient reach. Samples for both sites contained the leeches, water hog-louse and shrimp expected in perennial reaches and from WRC final effluents, along with the occasional winterbourne specialists including Nemoura lacustris (the winterbourne stonefly) and in samples we took back in 2006/7 some Paraleptophlebia werneri (the winterbourne mayfly).
What is perhaps more telling is the quality of the invertebrate community at Winterbourne Stoke about 2km downstream of Shrewton WRC. This site is fed by fairly reliable springs Ponded reach ds of WRC Dry channel though they do stop flowing in particularly dry years. We have sampled a site just upstream of the A303 annually since 2003 and samples consistently contain an abundance of taxa that are highly sensitive to organic pollution including Serratella ignita, Isoperla grammatica, Heptageniidae alongside a range of rare winterbourne specialists including Nemoura lacustris, Paraleptophlebia werneri, Limnephilus vittatus a caddisfly associated with drying sites, Synagapetus dubitans a caddisfly first recorded in the UK in 2010 and associated with spring fed sites, Agabus beetle larvae and occasionally the winterbourne black fly Metacnephia amphora.
The variety of both pollution sensitive and rare taxa that are regularly recorded at the site indicates that the Shrewton outfall is not causing a threat to the aquatic ecology of the River Till. We will continue to sample at Winterbourne Stoke along with four other sites on the River Till to maintain our long-term datasets that will allow any changes to be detected.
Water quality impact of Shrewton WRC
Ammonia levels within the River Till are unimpacted by the operation of the storm overflow. However, ammonia is not the only indication of water quality or assessment of impact.
We are currently undertaking an environment investigation into the operation of our assets (water recycling centres, storm overflows and abstractions) more widely across the Hampshire Avon catchment to better understand how we impact compliance with the Common Standards Monitoring Guidance, with respect to the Habitats Directive. This investigation will conclude in 2022 when findings will be discussed with the Environment Agency and any future investment needs identified will be included in our PR24 Business Plan, and subject to Ofwat approval. | [5 empty] | More information on this investigation
As part of this investigation, we are monitoring the water quality upstream and downstream of Shrewton WRC. We have reviewed all available historical data, collected by both Wessex Water and the Environment Agency, to date and this is being supplemented with twice monthly monitoring upstream and downstream of the final effluent (and storm overflow) discharge point at Shrewton WRC. From these data we have produced the following graphs illustrating river water quality during and outside of storm overflow operation:
For ammonia, there is no detectable difference between spill and no spill scenarios. Whether the storm tank is spilling or not, in most of the samples the ammonia concentrations are at the limit of detection. Total phosphorus increases slightly during a spill and with a greater range, although the mean (red dot) is slightly lower during spill events. However, the Soluble Reactive Phosphorus (SRP) concentrations in particular are low. The mean SRP concentration recorded during a spill is 0.03 mg/L which is the common standards monitoring guidance target for the Till, as determined by Natural England. Therefore, it’s not causing any appreciable impact to downstream water quality.
Solutions
To address this we have installed a reedbed to treat the increased flows to the site. The elevated flows are still screened and passed forward to the storm tank for settlement. This stormwater is settled and then flows into two new reedbeds which provide further treatment before being discharged into the River Till. The reedbeds were constructed in autumn/winter 2022 and first came into use in January 2023 to treat the settled stormwater. Due to the very dry summer in 2022 it took much longer than usual for the groundwater levels to rebound and the elevated flows to be seen at the WRC. We are routinely sampling the flows from the storm tank, into and out of these reedbeds to understand the water quality before it is discharged into the River Till.
The graphs below show recent water quality analysis of the crude sewage from the inlet to the water recycling centre, final effluent discharged to the river and then the settled stormwater flowing into and out of the reedbeds. This shows that even the influent is compliant with the final effluent permit (except for phosphorus), as well as the level of treatment through the water recycling centre and by the reedbed. Phosphorus concentrations in the reedbed treated storm flows are c.0.6mg/l, compared to the permit of 1mg/l and the final effluent concentrations during 2023 are <0.2mg/l.
Photo of the recently constructed reedbeds to treat the settled storm overflow. There are two reedbeds shown in the photo, in the foreground is reedbed 3 and at the back (slightly narrower) is reedbed 4. Both have been operational since groundwater flows were experienced at the site from 6th January 2023. |  |  |  |  | Photo showing a 'typical' crude sewage sample from Feb23 (far left, from Warminster WRC); then on the right, samples of the crude sewage at Shrewton WRC (left), SO reedbed effluent (middle) and fully treated final effluent (right). The reedbed effluent and final effluent are both discharged to the River Till.
Since we don’t have the rights to reline or seal private drains which connect to our public sewer, to reduce groundwater infiltration, we are exploring options to provide treatment of these more dilute but prolonged discharges. This reedbed is the only sustainable option to provide further treatment of storm waters prior to discharge into the Till.
We have one other example on the Langford Lakes Nature Reserve (see other case study), which provides treatment of discharges from the Hanging Langford pumping station, prior to discharge into the River Wylye. This is a very similar situation to Shrewton, on a similar geology, when groundwater inundation impacts the sewerage system for many months causing the site to overflow with dilute storm water. The treatment provided by the reedbed is such that it dilutes the River Wylye downstream of the discharge point having a positive impact on the watercourse, as well as relieving flooding for the villages and creating habitat within the reedbed itself.
We are currently preparing an Infiltration Reduction Plan for Shrewton which highlights further options for the village. | [5 empty] | More information
We are using the Event Duration Monitoring (EDM) data to determine where storm overflows are not operating as we would expect and investigating them through the Storm Overflow Assessment Framework. This provides a framework in which to identify storm overflows which discharge frequently and address the issues they cause through improvements. Since 2000 we have invested £181 million on upgrading 582 storm overflows across our region, with a further £150 million set aside for improvements between 2020 and 2025.
Storm Overflow Assessment Framework
Our plans for tackling overflows will in the future be documented in our Drainage and Wastewater Management Plans | [5 empty] | Drainage and Wastewater Management Plans
Videos showing the Shreston discgarge are linked to right. | [5 empty] | https://www.youtube.com/watch?v=iB0eGbgQPXo
https://www.youtube.com/watch?v=eipbAXBpnis
Water quality samples taken on 14/02/22. These show the stormwater through the treatment process from left to right, starting with the crude sewage at the inlet works and ending with the river water from the River Till downstream of the effluent discharge point (far right). The sample from the settled storm tank is the third from right.

## Hanging Langford Case Study
Case Study - Hanging Langford SPS
A case study in innovative permitting to resolve groundwater induced flooding of domestic properties.
Groundwater flooding
Hanging Langford lies in a chalk valley in Wiltshire straddling the river Wylye. In most winters the water table rises to ground level causing localised flooding. When this occurs, the sewerage system is effectively used as a land drainage network as residents have no option to protect their properties but to direct surface water down manholes. For many years the Environment Agency (EA) allowed Wessex Water, under emergency powers, to pump out the sewerage system to the local river in the village in order to provide a positive drainage system to the residents. This was not an officially permitted arrangement and overland temporary pumping made it very unsightly. Additionally, the area downstream included a network of lakes managed by the Wiltshire Wildlife Trust.
A pragmatic and sustainable solution
A new groundwater land drainage scheme would have been very expensive and only been beneficial for a few weeks in wet winters. Similarly, upsizing the sewer network’s capacity and the downstream sewage works would also have been very expensive and unsustainable. The solution involved an innovative permitting arrangement. After Wessex Water had ensured that its sewerage system was sealed, the EA agreed to permit a pumped, screened overflow only for periods when groundwater was about to cause flooding. A condition of the Permit was that Wessex Water provided a reed bed adjacent to one of the nature reserve lakes to treat the pumped storm flows prior to discharge to the Wylye. Sampling of the river upstream and downstream of the temporary overflow, and subsequently of the permanent overflow, shows that there is no adverse impact on the watercourse resulting from these occasional pumping operations. Wessex Water now works closely with Wiltshire Wildlife to manage the reed bed, which provides valuable habitat for a range of species such as dragonflies and warblers.
Map showing the location of the reedbed, on the Wiltshire Wildlife Trust Nature Reserve, with respect to the pumping station and previous discharge point into the River Wylye.
Progress
During 2022, we have worked with the Environment Agency to develop an Operating Techniques Agreement (OTA) approach to develop a permit for biologically treated intermittent discharges, such as this. From January 2023, we will undertake sampling, analysis, reporting and maintenance as agreed with the EA to demonstrate the level of treatment provided by this reedbed and it's appropriateness for as a long term and sustainable solution for this storm overflow. If successful, the status will change to a biologically treated intermittent permitted discharge, complying with numerical standards to demonstrate no adverse impact to the receiving environment.
Recent results show that the reedbed removes 72% of suspended solids found in the influent, with an average of 7mg/l in the reedbed effluent, and 88% removal of EColi.
Conclusion
In addition, we have been monitoring the River Wylye upstream and downstream of the reedbed discharge point. This shows that there is no impact on the river in terms of phosphorus or ammonia concentrations and a slight improvement in terms of Ecoli.
Inlet concentrations on 12/01/22 and 08/02/22 exceeded 1,000,000cfu.
Effluent 3,200 and 1,000cfu respectively
Sept 22 to Feb 23 identical upstream & downstream concentration
Upstream & downstream EColi concentration exceeded 3,000cfu/100ml on 03/11/21